| Journal Name: | Journal of Engineering Research and Reports |
| --- | --- |
| Manuscript Number: | Ms_JERR_144336 |
| Title of the Manuscript: | Research on the diagnosis of circulating current faults in the metal sheath of cross-linked XLPE cables under different working conditions |
| Type of the Article | Research |

| ## PART 1: Comments |  |  |
| --- | --- | --- |
|  | ## Reviewer’s comment Artificial Intelligence (AI) generated or assisted review comments are strictly prohibited during peer review. | Author’s Feedback (It is mandatory that authors should write his/her feedback here) |
| Please write a few sentences regarding the importance of this manuscript for the scientific community. A minimum of 3-4 sentences may be required for this part. | The purpose of this study is to conduct analysis of the distribution characteristics and variation laws of metal sheath circulating current in XLPE high-voltage single core cables with cross interconnection at 110 kV level under various typical fault conditions, in order to reveal their fault mechanisms and provide theoretical basis for state monitoring and protection strategies. | ## OK |
| Is the title of the article suitable? (If not please suggest an alternative title) | yes | ## OK |
| ## Is the abstract of the article comprehensive? Do you suggest the addition (or deletion) of some points in this section? Please write your suggestions here. | yes | ## OK |
| ## Is the manuscript scientifically, correct? Please write here. | yes | ## OK |
| Are the references sufficient and recent? If you have suggestions of additional references, please mention them in the review form. | yes | ## OK |
| ## Is the language/English quality of the article suitable for scholarly communications? | yes | OK |
| ## Optional/General comments | - The references must be numbered according to their sequence mentioning in the article body. - All equations require references. - Equations must be numbered as (1), (2), …and so on, not (2-1), (2-2),…. - Theoretical and simulation results of current are the same, both are theoretical. Comparison must be done between theoretical and practical results. - Measuring of open circuit voltage at the ends of open circuit must present to show the high voltage generated at the open ends of the cable. - Fault phase current is very huge, reaching to 10-18KA, how the author is measured it? - The simulation software must be explained and specified. | I will renumber the references and equations according to your suggestion. I will compare the theoretical and actual values of the circulation and explain in detail the simulation software used. I will indicate in the text the magnitude and impact of the open circuit voltage during an open circuit. When the fault phase current reaches the kA level, I scale the current through a current transformer for measurement, and then use relay protection and waveform recorder to cut off the fault and record the waveform. I will supplement these contents in the article. |

| PART 2: |  |  |
| --- | --- | --- |
|  | - Reviewer’s comment | Author’s Feedback (It is mandatory that authors should write his/her feedback here) |
| Are there ethical issues in this manuscript? | (If yes, Kindly please write down the ethical issues here in details) | There are no ethical issues with the manuscript. |