TECHNICAL EVALUATION OF POWER GENERATION MIX FOR RURAL ELECTRIFICATION: A CASE STUDY OF IMINI VILLAGE, OYO STATE, NIGERIA

Abstract:

This study was designed to evaluate the power generation mix for rural electrification in Imini Village, Oyo State, Nigeria, by analyzing eleven combinations of different Sustainable Stand-Alone Power Generation Alternatives (SSPGA). The alternatives comprised Wind Turbine (WT), Solar Power System (SPS), Diesel Generator (DG), and Polymer Electrolyte Membrane Fuel Cell (PEMFC), with the aim of determining the most cost-effective and environmentally friendly configuration. An energy audit and household energy profile were developed based on data collected from residents through structured questionnaires, in-depth interviews with artisans, and key informant interviews with community leaders. Simulation and sensitivity analyses of 11 scenarios were carried out using Levelised Cost of Energy (LCOE) and Net Present Cost (NPC) as key indicators of economic viability. The DG system was applied as the base case for comparison. The results revealed that the optimal hybrid configuration—WT + SPS + PEMFC—achieved an LCOE as low as $0.538/kWh and an NPC of $420,349.70, which was significantly lower than the costs associated with DG-only systems ($0.816/kWh, $637,366.80). It was further indicated that the average daily demand of 197.7 kWh and an annual AC primary load of 72,161 kWh were sufficiently met by the hybrid configuration, with CO₂ emissions reduced to zero in the optimal scenarios. The paper concludes that hybrid architecture based on WT, SPS, and PEMFC not only provides a cheaper per-unit cost of electricity but also ensures environmental sustainability compared to the DG-only system. This makes it a technically feasible and policy-relevant pathway for rural electrification in Nigeria.

Keywords: Power generation, Rural electrification, Levelised cost of energy, Net present cost, Hybrid power.

Introduction

Numerous studies in the past have shown that Nigeria houses abundant energy resources which include biomass, coal, crude oil, lignite, solar, hydropower, wind, geothermal, wood fuel and tidal energy. However, four of these resources (coal, crude oil, natural gas, and hydropower) are currently being actively used.  Among the many resources, solar energy and wood fuel are still primarily used in their raw forms, mainly for domestic cooking as well as heating (Otekunrin et al, 2021). Out of Nigeria’s total installed electricity generation capacity of 8,000MW, only 4,000 MW is currently operational (KPMG, 2022). In terms of electricity consumption in Nigeria, per capital is 167 kWh per person, ranking among the lowest globally (Doris Dokua Sasu, 2022).

The dire energy situation has hindered the country's development for decades, contributing to rising poverty levels as majority of businesses are crippled. According to the World Bank, the nation loses approximately $28 billion annually due to frequent power outages (Tosan Olajide, 2020). In response to this, many individuals and businesses rely on generators, which emit high levels of carbon and poses serious health risks to households and workers, while increasing the cost of living and further deteriorating the overall quality of life for Nigerians.

In order to lessen the continued impact of fossil fuels on climate change, a shift to renewable and sustainable energy sources is required. Traditional fossil fuels like oil are non-renewable and limited in supply. With the increasing demand for energy, the widening gap between this rising demand and the finite nature of oil must be addressed by expanding the use of alternative energy sources in the near future (Nwokocha et al., 2012, Zubairu et al; 2022).

As of 2017, the CO2 emissions per capital in developing nations including Nigeria accounted for 53% when compared to the industrialized nations, such as North America and Europe which contributed 18% and 17% respectively. However, this is expected to significantly increase as developing nations become industrialized (Our World in Data, 2017). In order to promote environmental sustainability and stable energy supply, the UN established a comprehensive energy policy to encourage the development of eco-friendlier fuels and promote renewable energy sources to reduce the carbon footprint (International Energy Agency, 2010, Zubairu et al; 2023). Previous studies on the use of alternative energy sources for power generation, for instance, Buragohain et al. (2021) carried out the technical, economic and environmental evaluation of a hybrid 3.5 kVA biogas-fueled generator and 1 kW solar photovoltaic plant (with battery backup). Their study examined energy sharing between the combined systems when the hybrid system was operated under constant load settings of between 20% to 80% of the rated power conditioning unit. Analysis using the System Advisor Model (SAM) showed a positive net present value of $306.45 and an LCOE value of $0.15/kWh for the electrical load demand of a residential community situated in a desert area.

Rehman and Al-Hadhram (2010) conducted a study on power generation in some hamlets around Rafha in Saudi Arabia, using a combination of solar PV, batteries and diesel. The solar irradiation data was collected on an hourly basis from the on-site. The PV modules were mounted on fixed platforms and four generators with different power rating, battery sizes and converters were used while diesel prices ranged from $0.2 to $1.2/L.

The results showed that the Cost of Energy (CoE) for a hybrid diesel/PV/battery system was $0.219/kWh, while a diesel-only system with 21% solar penetration had a slightly lower COE of $0.190/kWh when diesel was priced at $0.20/L.   However, as the price of diesel increased to $0.6/l, the CoE of the hybrid system approached that of the diesel-only system. When the diesel prices became higher than $0.6/l, the hybrid system (diesel/PV/battery) became more cost-effective than the diesel-only power system. Most existing studies have focused more on power generation for integration into the national grid, or using DG and renewable energy as backup solutions for rural communities (Zubairu et al; 2024). In contrast, this study, was designed to assess the energy needs of Imini village, Oyo State, Nigeria, and explore the feasibility of electrification through stand-alone power generation mix.

2. Materials and Methods

2.1 Information of Study Area

The selected off-grid remote rural village for this study is Imini. Imini community has about 80 households having a mean of five individuals in a household where they all generate power using fossil fuel generator. Major occupation of Imini residents is farming. Crops grown include: cocoa, kola nut, oil palm, tobacco, cassava, maize, citrus (orange, mango, and pineapple), melon and vegetables but they end up losing most of their farm produce to pest due to lack of sufficient electricity for processing . Because of the power challenges combating Imini community, most of their youths have migrated to cities such as Lagos, Ibadan, Oyo town etc., in search of educational, business and industrial opportunities. Presently, there are three (3) primary schools (2 publics and 1 private), one (1) public secondary school, one (1) health Centre, one (1) youth information Centre and one (1) solar powered borehole (dysfunctional) (Reshearcher,2023). The entire aforementioned infrastructures are presently in a very poor and dilapidated condition. Findings reveal that residents are being confronted on daily basis with problems such as lack of electricity, especially inadequate energy source for crop processing, no electricity to pump water needed for agricultural purposes, irrigation and households and industrial uses. This study therefore analyses the energy mix options for power generation at Imini based on their technical viability in terms of power production and consumption.

2.2 Qualitative Data Analysis Reports

2.2.1 Key informant and In-depth Interviews

In this study interview was conducted with residents as individuals and groups to get data on energy needs of the Imini residents by determining the energy audit and load profile of the community households. The study went further to investigate the spatial arrangement and social networks of the community as well as the resident perception about the problems they face in their community. Individuals and groups of selected people who participated in the planned discussion were asked questions about their perception, opinion, belief and attitude toward the energy need of the community. A structured questionnaire was administered to eighty household head (HH).  In-depth Interviews were conducted with 10 artisans, while Key Informant Interviews were held with four chiefs. These were processed and represented in this study statistically via excel sheet in form of load profile.

2.3 Scheduling of Electrical load

Load Profile

Having estimated the current and future (which are mainly their public utility needs) energy needs of the community based on the result of the audit conducted, energy profile was developed. As a result of the low income of the persons in the study community, the household energy demand of the village is assumed to be lower than that of the urban area. Analysis from Table 1.a indicates the proposed power consumption of basic household appliance and the number of hours used in a day per household which reflects the total kilowatt consumed at each particular hour and kilowatt-hour consumed by each electrical appliance in individual households. Result from Table 2.1b, shows the number of residential households in the community that is proposed to be connected to the power system. A total of 167.6 kWh daily energy demand is generated for the 80 households in Imini but a demand factor of 0.7 or 70% is used in ensuring that the system is properly sized and represents the characteristics of a community like Imini. The table also shows the effect of the application of the demand factor as seen in the Total Demand (kW) and Total Energy Demand (kWh) bringing the total Energy Demand for the 80 households in Imini to 117.30 kWh daily.

Table.1 The energy consumption profile of the appliances in each household in the community and their daily energy usage pattern

Table 2.: Number of Households and Demand Factor

Source: Researcher, (2017)

2.4. System components

A hybrid power system was designed for Imini village to generate electricity where the photovoltaic module was integrated with the wind turbine, electrolyser, hydrogen storage and fuel cell unit (figure 1). An auto-size back-up generator was also included in the configuration.

Figure 1.  Hybrid Power system

Source: Researcher, (2023)

A five year solar irradiation, and wind speed result of the study area (Akilo hills) was obtained from NIMET office. The HOMER software (Hybrid Optimization for Multiple Energy Resources) simulated power generation mix for scenarios 1 up to 11. The sensitivity variable parameter for simulation included 197.7kWh/d and 165kWh/d for electric load baseline average and electric load scaled average respectively and solar scaled average of 5.14kWh/m2/day. The Solar PV module used in the design has a capacity of 300 Watts per module. The entire array considered in this design amounts to 300kW and simulated using Homer optimizer. The modules were inclined at an angle of 15 degrees with a lifespan of 20 years. The capital and replacement costs were specified at $452/kW. No maintenance and operating cost was considered since little or no maintenance was needed for the panels to operate. Wind Turbine system was also proposed for this design. The XANT M-21-ETR  turbine with a capacity of 100 kW was used. The hub height of 31.80m was considered for the simulation. Clearly shown are the power curves of the wind turbine depicting how much power was generated.The cut in speed for the turbine is 3.0m/s while the rated wind speed and cut out wind speed is 11.0m/s and 20.0m/s respectively. The rotor diameter is 21.0m with 3 numbers blades. Its rotor speed is 58.0u/min and tip speed is 64m/s. The generator type for the turbine is permanent magnet produced at varying wind speeds.The capital and replacement costs of $80,000 were specified. The expected lifetime of the turbine is 20 years making it cheap and suitable for a 25 years project. Wind turbines are typically operational year-round with greater efficiency than other renewable energy sources and generate over 70% of their nominal year-round power output. It is worthy of note that according to Fadare 2010, the new generation wind turbines (like the XANT-M-21-ETR used in this study) have adequate capacity to work in light winds starting as low as 3m/s making wind a more viable and economical source of energy in most part of the north and mountains in the south. Polymer electrolyte membrane fuel cell was also proposed in the system design to compliment the wind and solar arrangement. The sensitivity analysis sizes considered in the optimization are 50 and 100kW for power generation. Electrolyser and Hydrogen tank for fuel supply has been embedded in the design as well. The lifetime hour for fuel cell operation is 40,000hours and cost per kilowatt is $3000.

The type of electrolyser employed for hydrogen production is also the polymer electrolyte membrane type. The size considered varied from 50kW to 70kW.The expected life time is 15years and operation efficiency is 85%. The cost per kilowatt is $1200.Stainless steel hydrogen tank storage was chosen for hydrogen storage. Hydrogen production was through water electrolysis using PEM electrolyser and stored for use by fuel cell to generate power for household and community use. An auto size generator of 54 kW was used as the baseline modelling datapoint. This baseline modelling data point helps to determine cost and the rating.The price of diesel considered is $0.65 equivalent. The auto size generator operates at a minimum load ratio of 25% and 15,000 lifetime hours.

Figure 2: Equipment configuration for Imini hybrid power system

Source, Researcher, (2017)

2.5 Optimization of the System

The basis for electricity consumption and production was formed using the present and future electric load demand for the community derived from the energy profile and input parameters of the system architecture.

2.5.1. Model Assumption:

Availability of adequate renewable energy resources at Imini Village

The assumption was that the Village has access to renewable energy resources such as solar, wind and hydro that can be harnessed for power generation. The assumption is that these resources are viable and available in sufficient quantities to meet the energy demands of the rural community.

This assumption is important because HOMER Pro Software is widely used for analyzing and optimizing hybrid power systems that combine multiple renewable energy sources with conventional power sources. It helps determine the optimal mix of energy sources based on resource availability, cost, and other factors.

These assumptions would further shape the modeling and analysis conducted using HOMER Pro Software for designing an effective and sustainable power generation mix for rural electrification. However, summary information has been included in Table 2.1 to enhance transparency.

## Table 2.1: Summary of Key Modelling Assumptions

| Parameter | Assumption | Justification |
| --- | --- | --- |
| Fuel Cell Lifetime | 15 years | Based on literature values for PEMFC operational life in hybrid systems. |
| Solar PV Lifetime | 25 years | Consistent with manufacturer specifications and prior HOMER-based studies. |
| Wind Turbine Lifetime | 20 years | Aligned with global wind industry benchmarks for small/medium systems. |
| Diesel Generator Lifetime | 15,000 operating hours | Standard operational benchmark from field data and manufacturers. |
| Discount Rate | 8.0% | Reflects average national interest rate and rural electrification project standards. |
| Fuel Cost (Diesel) | $1.10/litre | Based on prevailing market rates during the study period in Nigeria. |
| Solar Irradiance Data | 14.4 – 21.7 MJ/m²/day | Derived from Nigerian Meteorological Agency 5-year averages (2013–2017). |
| Wind Speed Data | 4 – 9 m/s | Derived from Nigerian Meteorological Agency 5-year averages (2013–2017). |

Source: Researcher, (2017)

2.5.2 Mathematical Modeling for the Hybrid Power System

The modeling of the SSPGA components is given below.

#### Solar PV Panel

The photovoltaic current (Iph) under standard test conditions (STC) given by the manufacturer (Tref = 298.15 K (25 °C) and Gref = 1000 W/m2) is given by (2.1):

𝐼𝑝ℎ=[𝐼𝑠𝑐+𝐾𝑖(𝑇−𝑇𝑟𝑒𝑓)]×𝐺/1000                                     2.1

where T, G, Isc, and 𝐾𝑖 are the operating temperature, solar irradiance, short-circuit current, and coefficient with temperature of the short-circuit current, respectively.

The PV panel voltage is given by (2.2):

𝑈𝑃𝑉=𝑈𝐷𝐶×𝑁𝑠                                                           (2.2)

where UDC is the cell voltage and Ns is the number of cells connected in series.

The power (P) generated by the PV is given by (2.3):

𝑃=𝐼𝑠𝑐×𝐺×𝑈𝑃𝑉×𝑁𝑠/𝑘𝐹                                                   (2.3)

where 𝑘𝐹 represents the loss factor.

#### Wind Turbine

The power generated by a wind turbine is given by (2.4):

𝑃𝑚𝑎𝑥=16/27×𝑃0                                                                                       (2.4)

where 𝑃0  is the power on the upstream section

𝑃0=1/2×𝜌×𝐴𝑟×𝑣03                                                           (2.5)

and 𝜌 is air density [kg/m3], 𝐴𝑟 is the area swept by the rotor blades [m2], and 𝑣0 is the wind speed [m/s].

So

𝑃𝑚𝑎𝑥=0.296×𝜌×𝐴𝑟×𝑣03                                                                       (2.6)

Pmax denotes the theoretical maximum power produced by the Wind turbine

#### Fuel Cell

Fuel cells (FC) are devices that use electrochemical oxidation-reduction reaction to perform the direct conversion of chemical energy into electrical energy, which occurs at the two electrodes, namely, the anode that is supplied with hydrogen (H2) and the cathode that is supplied with oxygen (O2) from air, and are separated by an electrolyte that allows the transfer of ions between the two electrodes. Based on the nature of electrolyte or fuel used, there are different types of cells, among which the proton exchange membrane fuel cell (PEM-FC) is widely used due to its low temperature operation and fast start-up.

The output voltage of the fuel cell is given by the following equation (2.7):

𝑉=𝐸−𝑉𝑎𝑐𝑡1−𝑉𝑐−𝑉𝑜ℎ𝑚                                                                            (2.7)

where 𝐸 is the internal voltage of the fuel cell (FC), 𝑉𝑎𝑐𝑡1 is the temperature-dependent activation voltage loss, 𝑉𝑐 is the voltage loss across the capacitor, and 𝑉𝑜ℎ𝑚 is the voltage loss across the ohmic resistance.

The voltage E across a single cell is given by the following relationship:

𝐸=𝐸0+𝑅𝑇/2(𝑃𝐻2𝑃𝑂2/ 𝑃𝐻2𝑂)………………………………….    2.8

where 𝐸0 =1229 V is the standard potential of the hydrogen/oxygen reaction, R is the universal gas constant, F is the Faraday’s number, 𝑃𝐻2 is the partial pressure of hydrogen at the anode,  and 𝑃𝐻2𝑂 and 𝑃𝑂2 are the partial pressures of water and oxygen at the cathode, respectively.

2.5.3 Theory of HOMER

The theory behind HOMER involves performing a techno-economic analysis that considers the costs, performance, and availability of different energy resources and technologies. The software uses optimization algorithms to determine the optimal configuration and dispatch strategy for the hybrid power system.

The basic objective function of HOMER is to minimise the total net present cost (NPC) of the system over the analysis period, which includes the capital costs, operating costs, and replacement costs of the different system components (NREL, 2021). The NPC is calculated using the formula:

NPC = IC + OC + RC + FC + VC ……………………………………………… 2.9

Where:

IC: Initial capital costs of the system components

OC: Operating costs, including maintenance, fuel, and other expenses

RC: Replacement costs of components with a finite lifespan

FC: Financial costs, such as interest and loan payments

VC: Value costs, which account for factors like emissions and environmental impacts

HOMER takes into account various constraints and parameters, including the energy demand profile, the availability and variability of renewable energy resources, the technical specifications and efficiency of different technologies, and the desired level of reliability.

2.5.4 Calculating Levelised Cost of Energy in HOMER

The levelised cost of energy (LCOE) in HOMER (Hybrid Optimization for Multiple Energy Resources) is calculated using the following formula:

LCOE = (Total annualized costs / Total annual energy production) + (Total annualized costs * O&M costs).

LCOE = (TAC / TAEPr) + (TAC * O&MC) …………………………………….. 2.10

Where:

Total annualized costs: The sum of the annualized capital costs and the annualized O&M costs.

Total annual energy production: The total amount of energy produced in a year by the system.

O&M costs: The annual operation and maintenance costs as a percentage of the capital costs.

The annualized capital costs can be calculated as follows:

Annualized capital costs = (Capital cost * CRF) / Lifetime

ACC = (CC * CRF) / LT …………………………………………………………… 2.11

Where:

Capital cost: The initial cost of the system.

CRF: The capital recovery factor, which is calculated as (r(1+r)^n) / ((1+r)^n - 1), where "r" is the discount rate and "n" is the system lifetime.

Lifetime: The expected lifetime of the system.

2.5.5 Estimation of Carbon Emission in HOMER

To estimate carbon emissions associated with electricity generation in HOMER, the following expression can be followed:

Total Carbon Emissions = (Energy Production₁ * Emissions Factor₁) + (Energy Production₂ * Emissions Factor₂) + ... + (Energy Productionn * Emissions Factorn)

EP₁ * EmF₁) + (EP₂ * EmF₂) + ... + (EPn * EmFn) ………………………………….. 2.12

Where:

Energy Production₁, Energy Production₂, ... Energy Productionn is the annual energy production for each energy source in the system.

Emissions Factor₁, Emissions Factor₂ ... Emissions Factorn: is the emissions factor (expressed as CO2 emissions per unit of energy) for each energy source.

3. Results and Discussions

3.1 Wind system only with auto size generator back up (Scenario 1)

The results show that the auto size generator contributes 6.90 percent of the entire electricity while the Wind turbine contributes about 93.1 percent of the design capacity (Table 3).The total annual production of the system is 484,362kWh/yr while the AC primary load of the community is 72,161kWh/yr this suggests that there is sufficient production to meet the energy demand of the community and excess is also generated for the purpose of scale up in the future and feeding of neighboring communities and by extension functioning as base station for feed back into national grid in the future.

Auto Size Generator

From the results the mean electrical output for auto size generator was 14kW while the maximum electrical output was 31.5kW and its average electrical efficiency was 23.7% on 2,389hrs/yr for operational hours and with operational life time of 6.28 years and rated capacity factor of 7.06% at fixed generation cost of $3.37/hr.

Wind Turbine Result

In the hybrid design of the Imini community, an AC wind turbine was used in the simulation. The XANT M-21-ETR wind turbine with rated capacity of 100 kW was selected as the wind turbine to produce the optimum or most efficient output. The mean output for the Wind turbine system is 51.5kW and maximum output is 98.1kW.  This is largely due to the wind speed of Akilo hill which is approximately a yearly average of 8m/s. The total production from the wind turbine is 450,944kWh/yr with yearly hours of operation of 7817hr/yr. The LCOE for wind turbine system alone is $0. 0192kWh which makes the use of wind resources cheap and highly competitive. The Wind turbine data output in Figure 3, clearly shows the color representation and implies that turbine operates for 24 hours every day with significant impact of wind penetration being felt almost across the day. As explained earlier, this is largely due to the wind speed resource on Akilo hill at the Imini community. The optimal hybrid configuration—WT + SPS + PEMFC—achieved an LCOE as low as $0.538/kWh.

Table 3 Power production and consumption (Scenario 1)

| Power generation mix | Total Consumption(kWh/yr) | Electrical Output(kWh/yr) | Total output(kWh/yr) | System Architecture(kW) |
| --- | --- | --- | --- | --- |
| 1 | 72,161 | Gen-33,418,WT - 450,944 | 484,362 | Gen – 54, WT- 100 |

Figure 3. XANT M-21-ETR [100kW] Production (kW)

3.2 Solar PV only with Auto size generator back up (Scenario 2)

The results show that the auto size generator contributes 34.1 percent of the entire electricity while the Solar PV contributes about 65.9 percent of the design capacity.The total annual production of the system is 235,967kWh/yr (Table 4) while the AC primary load of the community is 72,161kWh/yr this suggests that there is sufficient production to meet the energy demand of the community and excess is also generated for the purpose of scale up in the future and feeding of neighboring communities and by extension functioning as base station for feed back into national grid in the future.

Auto Size Generator Result

The auto size generator scoring rate is 34.1% with mean electrical output of 15.1kW and 32.5kW maximum output for mean electrical efficiency of 24.5% at 5,320hrs/yr of operation while the specific fuel consumption for the generator is 0.414L/kWh.The operational life of the generator is projected at 2.82 years with capacity factor of 17%.  The generator operates at almost zero capacity during the day but functions at 26-35kW between 6pm and 12am at fixed generation cost of $3.37/hr.

PV Result

The table 4 clearly showed the rated capacity of Nexus flat plate PV is 102kW, from the electrical result, the mean output is 17.8kW and 426kWh/d while total production of 155,619kWh/year which exceeds the AC primary load of the community thus sufficient enough to meet their energy need. The Levelized Cost of Energy (LCOE) for the solar PV is $ 0.0295/kWh and the total number of hours of operation is 4,318hr/yr with Photovoltaic Infiltration of 258 percent. The d map chart (Figure 4) shows in color variations the power output of the array in each time step of the year with production occuring between 6am and 7pm daily also from data map output chart, PV operates at 48-96kw between 6am and 6pm daily.

The cost of operation and fueling which stands at $111,415 and $279,771 respectively contributes to the rises in the LCOE for this arrangement.

Table 4 Power Production and Consumption (Scenario 2)

| Power generation mix | Total Consumption(kWh/yr) | Electrical Output(kWh/yr) | Total output(kWh/yr) | System Architecture(kW) |
| --- | --- | --- | --- | --- |
| 2 | 72,161 | PV-155,619, Gen -80,348 | 235,967 | PV – 102, Gen- 54 |

Figure 4. Nexus flat plate PV Production (kW)

3.3 Wind and Solar Photovoltaic only with Generator back up (Scenario 3)

Table 5 indicates that the photovoltaic (PV) capacity in the hybrid configuration is minimal, with only one wind turbine included, while a 54 kW auto-sized generator serves as backup. The system is heavily dominated by wind performance, contributing 92.9% of the total share compared to just 0.27% from PV, underscoring the site’s strong wind potential. The generator, accounting for 6.87% of the system, supports up to 31.5 kW capacity, with a mean electrical output of 14.0 kW, mean efficiency of 23.7%, and specific fuel consumption of 0.429 L/kWh over 2,385 operating hours annually. With a capacity factor of 17% and a projected lifespan of 6.29 years, the generator provides flexible support by operating between 13.5–31.5 kW as needed, highlighting the comparative dominance of wind energy, the marginal role of PV, and the generator’s crucial backup function to stabilize the hybrid arrangement.

PV Result

Maximum power output for Solar PV is 0.87kW with operating hours of 4,318 yearly deplorable to meet energy demand in school during the day. Solar PV mean output is 0.150kW and 3.59kWh/d. The peak performance of between 0.60-0.80kW usually occurs between hours of 10am to 4pm daily

Wind Turbine Result

The mean output for the Wind turbine system is 51.5kW and maximum output is 98.1kW resulting from wind infiltration of 747 percent on Akilo hill. The total production from the wind turbine is 450,944kWh/yr with yearly hours of operation of 7817hr/yr. The LCOE for wind turbine system is $0. 0192kWh which is cheaper when compared to Solar PV. The Wind turbine output chart (Figure 5) clearly shows the distribution of 24 hours every day output with significant impact.

Table 5 Power Production and Consumption (Scenario 3)

| Power generation mix | Total Consumption(kWh/yr) | Electrical Output(kWh/yr) | Total output(kWh/yr) | System Architecture(kW) |
| --- | --- | --- | --- | --- |
| 3 | 72,161 | PV – 1,310, Gen-33,364 WT – 450,944 | 485,618 | PV – 0.859, Gen – 54 WT - 100 |

3.4 Wind and Fuel cell with Auto Size Generator back up (Scenario 4)

The system architecture comprised 54kW generator, 50kW PEM Fuel cell, 100kW XANT M-21-ETR wind turbine and other components such as 50kW PEM Electrolysis device and 700kg hydrogen container. From the electrical result in table 6, the PEM fuel cell has scoring value of 2.45% and Wind turbine scoring is 97.6%. The auto size generator scoring value is 0% which implies that auto size generator does not contribute to the power generation for this scenario.

Autosize Generator Result

Result showed that the auto size generator power output showed all round black coloration which implies 0kW power output (Figure 6).

Figure 6. Autosize Genset Output (kW)

Fuel Cell Result

The simulation data showed the fuel cell result for Hybrid system in the Imini community power generation mix. The mean electrical output of fuel cell is 4.74kW with expected operational life of 16.7years and operating hours of 2,389hrs/yr.Fuel cell production is 11,317kWh/yr which is enough to take care of certain percentage of the community household demands. The fuel cell result from the fuel cell power output showed it worked to supplement the wind turbine where the village's power demand rises between 6 pm and 12 am, delivering between 20-31kW as shown in Figure 7. Electrolyser functions as energy storage in this scenario when there is excess electricity and hydrogen from the storage is supplied to fuel cell to compliment wind turbine when there is power deficiency.

Figure 7.  PEM Fuel Cell Output (kW)

Wind Turbine Result

The mean output for the Wind turbine system is 51.5kW and maximum output is 98.1kW. The total production from the wind turbine is 450,944kWh/yr with yearly hours of operation of 7817hr/yr (Table 6).The LCOE for wind turbine system is $0. 0192kWh which is cheaper when compared to Solar PV. The Wind turbine output data map (Figure 8) clearly shows the colour representation and implies that the wind turbine was operating at optimum

Table 6. Power Production and Consumption (Scenario 4)

| Power generation mix | Total Consumption(kWh/yr) | Electrical Output(kWh/yr) | Total output(kWh/yr) | System Architecture(kW) |
| --- | --- | --- | --- | --- |
| 4 | 121,131 | Gen – 0, PEMFC – 11,317 WT – 450,944 | 462,261 | Gen – 54, PEMFC –50 WT -100 |

Figure 8.   XANT M-21-ETR [100kW] Production (kW)

3.5 Solar PV and Fuel cell with Auto Size Generator back up (Scenario 5)

Result from table 7 revealed that the size of PV is 124kW and PEM fuel cell is 50kW with an auto size generator of 54kW as backup to supply power for 24 hours. PV power production is 189,536 which represent a scoring rate of 79.5% and PEM fuel cell power production is 48,990kWh/yr representing 20.5% scoring value. The use of auto size generator for this arrangement is negligible or equals to zero. Total power production from solar PV and fuel cell was 238,526kWh/yr enough to meet the primary energy demand of the community without the need for a generator back up

Fuel Cell Result

Fuel cell electrical summary revealed that the system operated at 50 percent efficiency with annual production of 48,990kWh/yr. The mean electrical output is 32.5kW and hydrogen fuel consumption value is 2,939kg with specific fuel consumption of 0.0600kg/kWh. Operational hours of fuel cell for this architecture is 5,191hrs/yr with optimum operation occurring between 6pm to 12am at power output of 14-32kW (Figure 9). Electrolyser mean output is 0.336kg/hr and total production is 2,943kg/yr (more than Fuel cell, hydrogen consumption requirement of 2,939kg). The electrolyser produces hydrogen by drawing power from Solar PV to supply fuel cell for Night use and also to make up for power supply shortfall from Solar PV.

Figure 9.  PEM Fuel Cell Production (kW)

PV Result

Result showed the rate capacity of Nexus flat plate PV is 124kW, from the electrical result, the mean output is 21.6kW and 519kWh/d while total production of 189,536kWh/year. The Levelized Cost of Energy (LCOE) for the solar PV is $ 0.0295/kWh and the total number of hours of operation is 4,318hr/yr with Photovoltaic Infiltration of 314 percent (Table 7). The d map chart (Figure 10) shows in color variations the power output of the array in each time step of the year with production occuring between 6am and 7pm daily also from data map output chart, PV operates at 50-126kw between 6am and 6pm daily.

Table 7 Power Production and Consumption (Scenario 5)

| Power generation mix | Total Consumption(kWh/yr) | Electrical Output(kWh/yr) | Total output(kWh/yr) | System Architecture(kW) |
| --- | --- | --- | --- | --- |
| 5 | 196,965 | PV – 189,536, Gen – 0 PEMFC – 48,990 | 238,526 | PV – 124, Gen – 54 PEMFC - 50 |

Figure 10.  Nexus flat plate PV Production (kW)

3.6 Fuel cell system with auto size generator back up (Scenario 6)

The size of PEM fuel cell for this arrangement (Table 8) is 100kW as well as 50kW Electrolysis device, 700kg Hydrogen container, to be backed up by 54kW auto size generator.

Auto Size Generator Result

From the auto size generator electrical result, electrical production was 126,993kWh/yr enough to meet AC electrical power demand of 72,161kWh/yr for Imini community. The mean electrical output was 14.5kW and the yearly diesel fuel consumption was 53,571/L with average electrical efficiency of 24.1 percent. The operational hour of the auto size generator is 8,760hr/yr and operational life time of 1.71 years.

Fuel Cell Result

This system was predominantly dominated by auto-size generator with zero fuel cell penetration even though the cost of fuel cell reflected in the overall cost result analysis thereby adding to the NPC and the LCOE of the system.

Table 8 Power Production and Consumption (Scenario 6)

| Power generation mix | Total Consumption(kWh/yr) | Electrical Output(kWh/yr) | Total output(kWh/yr) | System Architecture(kW) |
| --- | --- | --- | --- | --- |
| 6 | 89,621 | Gen – 126,993 PEMFC- 0 | 126,993 | Gen – 54 PEMFC- 100 |

3.7 Wind, Solar PV and Fuel cell with Auto Size Generator (Scenario 7)

The hybrid system architecture comprises a 54 kW auto-sized generator, 50 kW PEM fuel cell, 100 kW wind turbine, 0.890 kW Nexus flat plate PV, a 700 kg hydrogen container, and a 50 kW PEM electrolyzer. Power generation is strongly dominated by the wind system, producing 450,944 kWh/yr (97.3%), while the fuel cell contributes 11,182 kWh/yr (2.41%) and solar PV only 1,358 kWh/yr, highlighting the overwhelming reliance on wind and the minimal role of PV. Unlike the previous configuration, the auto-sized generator makes no contribution here, eliminating diesel-related costs. The PEM fuel cell operates at 50% efficiency, with a maximum electrical output of 31.5 kW, mean output of 4.69 kW, and specific fuel consumption of 0.0600 kg/kWh over 2,385 annual operating hours, sustaining a lifespan of 16.8 years. Its role is pivotal in mitigating intermittency, particularly between 6 pm and 12 am, where it supports output in the 14–31.5 kW range. The electrolyzer, powered by wind energy, supplies hydrogen storage for fuel cell operation, positioning the fuel cell as both generator and storage medium, thereby strengthening system resilience compared to configurations reliant on diesel backup.

Figure 11 PEM Fuel Cell Production (kW)

PV Result

Result revealed that Nexus flat plate PV has mean output of 0.155kW and 3.72kWh/d which is very low compared to the Wind system. The low percentage input of solar PV in the arrangement is characterised by lower LCOE cost for wind power as well as high wind infiltration in the system and absence of battery storage in this arrangement.

Wind Turbine Result

It could be seen that the wind turbine has mean output of 51.5kW and maximum output of 98.1kW. The levelised cost of energy for wind system is 0.0192kWh and this contributes to bringing down the value of the overall LCOE for the hybrid system. Operational hours for the wind turbine are 7,817hrs/yr). Result also indicated that the wind turbine operates for 24hours at varying output to meet the energy needs of the community.

Table 9 Power Production and Consumption (Scenario 7)

| Power generation mix | Total Consumption(kWh/yr) | Electrical Output(kWh/yr) | Total output(kWh/yr) | System Architecture(kW) |
| --- | --- | --- | --- | --- |
| 7 | 120,756 | PV – 1,358, Gen – 0 PEMFC – 11,182 WT – 450,944 | 463,485 | PV – 0.809, Gen – 54 PEMFC – 50 WT – 100 |

3.8 Generator only (as base case and Scenario 8)

This forms the base case for this study and it includes Generator only system since the community depends on the use of generator only at the moment for their power supply.

Result from table 10 revealed electrical power production of 126,993kWh/yr sufficient to meet the AC primary load demand of the Imini community.

Auto Size Generator Result

Also, power is 126,993kWh/yr with operational hours of 8,760hrs per year.  The generator is expected to function for 1.71years with capacity factor of 26.8 %.

Table 10 Power Production and Consumption (Scenario 8)

| Power generation mix | Total Consumption(kWh/yr) | Electrical Output(kWh/yr) | Total output(kWh/yr) | System Architecture(kW) |
| --- | --- | --- | --- | --- |
| 8 (Base case) | 72,161 | Gen-126,993 | 126,993 | Gen- 54 |

3.9 Solar PV system and Fuel cell (Scenario 9)

The size of solar PV is 124kW and PEM fuel cell is 50kW with 50kW PEM electrolyser for hydrogen production and 700kg hydrogen container for storage. Nexus Solar PV produces 189,536kWh/yr while 48,990kWh/yr is the production from PEM fuel cell as shown in table 11.

Fuel Cell Result

PEM fuel cell mean output is 9.44kW and has 5,191hrs/yr of operation, operating mainly between 12am to 8am and 6pm till 12 am.

PV Result

Result revealed that the mean output for Nexus PV is 21.6kW and 519kWh/d for 4,318hrs/yr hours of operation. The LCOE for solar PV alone is $0.0295kWh which contributes to the reduction in the LCOE for the overall hybrid arrangement. Operating hours for the Solar PV from the output graph (Figure 12) is 7am to 8pm in the evening but on the peak of operation between 10am and 4pm.

Table 11. Power Production and Consumption (Scenario 9)

| Power generation mix | Total Consumption(kWh/yr) | Electrical Output(kWh/yr) | Total output(kWh/yr) | System Architecture(kW) |
| --- | --- | --- | --- | --- |
| 9 | 196,965 | PV – 189,536 PEMFC – 48,990 | 238,526 | PV – 124 PEMFC – 50 |

Figure 12. Nexus flat plate PV Production (kW)

3.10 Wind System and Fuel Cell (Scenario 10)

The size of Wind turbine for the system is 100kW capacity and 50kW PEM fuel cell with 50kW PEM electrolyser and 700kg hydrogen container (Table 12). Energy production for wind turbine and fuel cell is 450,944 and 11,317kWh/yr respectively.

Fuel Cell Result

Fuel cell mean output from result is 4.74kW and operational hours are 2,389hr/yr and fixed generation cost is $4.38/hr.

Wind Turbine Result

The Wind turbine output data map (Figure 13) clearly shows the colour representation that implies the wind turbine was working at optimum. The wind turbine operates at 7,817hr/yr with mean output of 51.5kW.

Table 12 Power Production and Consumption (Scenario 10)

| Power generation mix | Total Consumption(kWh/yr) | Electrical Output(kWh/yr) | Total output(kWh/yr) | System Architecture(kW) |
| --- | --- | --- | --- | --- |
| 10 | 121,131 | PEMFC – 11,317 WT – 450,944 | 462,261 | PEMFC – 50 WT – 100 |

Figure 13 XANT M-21-ETR [100kW] Production (kW)

3.11 Wind, Solar PV and Fuel Cell system (Scenario 11)

This consists of the hybrid of Wind turbine, Solar PV and PEM fuel cell which is 100% renewable technology.

The power output of Solar PV is low compared to Wind and Fuel cell because of the absence of battery storage for the Solar PV system and also because the rate of power demand during the day is low compared to power demand during the night period. Fuel cell is proposed to take of intermittency in the system. The power from the Nexus PV system will be utilised in the schools during the school hours and it will be complimented with fuel cell power while the energy demand for the other sectors of the village will be met by Wind system and Fuel cell. The low cost of Wind energy system and high-power production has made this option more economical than the use of generator only option as the case of scenario 8 which is used as the base case for this power generation mix analysis.

Result from table 13 showed that the power production from wind system, fuel cell system and solar PV were 450, 944, 11,182 and 1,358 kWh/yr respectively sufficient enough to catch up with the energy need of the community without the need for a generator back up and there is fuel cell availability to support wind and solar PV in case of intermittency which would have been the reason for compulsory use of a storage battery in the system. The energy production is sufficient enough to meet the 72,161kWh/yr AC primary load of the village. The unmet electric load is 0kWh/yr and capacity shortage is also 0kWh/yr

Table 13 Power Production and Consumption (Scenario 11)

| Power generation mix | Total Consumption(kWh/yr) | Electrical Output(kWh/yr) | Total output(kWh/yr) | System Architecture(kW) |
| --- | --- | --- | --- | --- |
| 11 | 120,756 | PV – 1,358 PEMFC – 11,182 WT – 450,944 | 463,485 | PV – 0.890 PEMFC – 50 WT – 100 |

Fuel Cell Result

Result showed that PEM fuel cell has maximum electrical production of 31.5kW and 2385hrs/yr of operation over 16.8years lifetime, operating lightly in morning and afternoon as back up and more intensely in the evening especially between 6pm and 12am (Figure 14).

Figure 14.  PEM Fuel Cell Production (kW)

PV Result

Result also revealed that the mean output for Nexus PV is 0.155kW and 3.72kWh/d for 4318 hrs/yr hours of operation. The LCOE for solar PV alone is $0.0295kWh which contributes to the reduction in the LCOE for the overall hybrid arrangement. Operating hours for the Solar PV from the output graph (Figure 15) is 7am to 6pm in the evening but on the peak of operation between 10am and 4pm.

Figure 15. Nexus flat plate PV Production (kW)

Wind Turbine Result

The wind turbine has mean output of 51.5kW and maximum output of 98. 1kW from the result obtained. The levelised cost of energy for wind system is 0.0192kWh and this contributes to bringing down the value of the overall LCOE for the hybrid system. Operational hours for the wind turbine are 7,817hrs/yr. The wind turbine operates for 24hours (Figure 16) at varying output to meet the energy needs of the community.

Figure 16. XANT M-21-ETR [100kW] Production (kW)

# 3.12 Electrical Energy Consumption and Production Summary

Electrical consumption and production for the power generation mix is discussed in Table 14

Table 14  Electrical Consumption and Production Results

| Power generation mix | Total Consumption(kWh/yr) | Electrical Output(kWh/yr) | Total output(kWh/yr) | System Architecture(kW) |
| --- | --- | --- | --- | --- |
| 1 | 72,161 | Gen-33,418,WT - 450,944 | 484,362 | Gen – 54, WT- 100 |
| 2 | 72,161 | PV-155,619, Gen -80,348 | 235,967 | PV – 102, Gen- 54 |
| 3 | 72,161 | PV – 1,310, Gen-33,364 WT – 450,944 | 485,618 | PV – 0.859, Gen – 54 WT - 100 |
| 4 | 121,131 | Gen – 0, PEMFC – 11,317 WT – 450,944 | 462,261 | Gen – 54, PEMFC –50 WT -100 |
| 5 | 196,965 | PV – 189,536, Gen – 0 PEMFC – 48,990 | 238,526 | PV – 124, Gen – 54 PEMFC - 50 |
| 6 | 89,621 | Gen – 126,993 PEMFC- 0 | 126,993 | Gen – 54 PEMFC- 100 |
| 7 | 120,756 | PV – 1,358, Gen – 0 PEMFC – 11,182 WT – 450,944 | 463,485 | PV – 0.809, Gen – 54 PEMFC – 50 WT – 100 |
| 8 (Base case) | 72,161 | Gen-126,993 | 126,993 | Gen- 54 |
| 9 | 196,965 | PV – 189,536 PEMFC – 48,990 | 238,526 | PV – 124 PEMFC – 50 |
| 10 | 121,131 | PEMFC – 11,317 WT – 450,944 | 462,261 | PEMFC – 50 WT – 100 |
| 11 | 120,756 | PV – 1,358 PEMFC – 11,182 WT – 450,944 | 463,485 | PV – 0.890 PEMFC – 50 WT – 100 |

3.13 Emission Results

Table 15 Emission Summary

| Toxic substances | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Carbon (IV) Oxide (kg/yr) | 37,492 | 87,152 | 37,430 | 0 | 0 | 140,227 | 0 | 140,227 | 0 | 0 | 0 |
| Carbon (II) Oxide (kg/yr) | 236 | 549 | 236 | 0 | 0 | 884 | 0 | 884 | 0 | 0 | 0 |
| Unscathed Hydrocarbons (kg/yr) | 10.3 | 24.0 | 10.3 | 0 | 0 | 38.6 | 0 | 38.6 | 0 | 0 | 0 |
| Particulate Matter (kg/yr) | 1.43 | 3.33 | 1.43 | 0 | 0 | 5.36 | 0 | 5.36 | 0 | 0 | 0 |
| Sulfur (IV) Oxide (kg/yr) | 91.8 | 213 | 91.7 | 0 | 0 | 343 | 0 | 343 | 0 | 0 | 0 |
| Nitrogen Oxides (kg/yr) | 222 | 516 | _ | 0 | 0 | 830 | 0 | 830 | 0 | 0 | 0 |

Table 16 shows the emission summary for scenarios 1 to 11 highlighting scenario 8 which is also the base case as the basis for comparison with the other scenarios.  Fuel and emission result for scenario 11 showed a clean energy system with zero emission of toxic substances and no diesel consumption. This denotes that the power mix arrangement for Imini community is environmentally friendly.

3.14 NPC AND LEVELISED COST OF ELECTRICITY

Table 16 Analysis of the economics of the power generation mix for all the scenarios in comparison with the base case.

| Scenario | NPC ($) | LCOE($/kWh) |
| --- | --- | --- |
| 1 | $285,764.20 | $0.366 |
| 2 | $454,111.60 | $0.582 |
| 3 | $285,981.00 | $0.366 |
| 4 | $423,549.90 | $0.543 |
| 5 | $539,126.80 | $0.691 |
| 6 | $966,200.40 | $1.24 |
| 7 | $423,851.50 | $0.543 |
| 8 | $637,366.80 | $0.816 |
| 9 10 | $535,624.90 $420,048.10 | $0.686 $0.538 |
| 11 | $420,349.70 | $0.538 |

# The result from table 16 revealed a cheaper LCOE for scenario 11 when compared with the base case (scenario 8) of fossil fuel generator use only.  The NPC of $420,349.70, which was significantly lower than the costs associated with DG-only systems ($0.816/kWh, $637,366.80).

3.15 Conclusion

The designed hybrid power system was able to optimise the power generation mix of Imini standalone system and it can be said to be feasible, more environmental friendly, sustainable and a good economic option. More so, renewable energy sources are reliable. And it is speculated that by year 2050 world oil reserve would be insufficient to cater for fast growing global economy hence focus now on renewable energy economy before the time (Reuters, 2021). The results gotten in HOMER demonstrates that component sizes cost summary, cash flow summary, electrical production and cost of PV-Wind-Fuel cell hybrid system has been found feasible. Considering the hybrid system comparison with the base case of diesel generator use only, it is concluded that the standalone hybrid system proposed for the Imini community is feasible and a good economic option.

Among the 11 simulated scenarios, the Wind Turbine + Solar Power System + Proton Exchange Membrane Fuel Cell configuration emerged as the most sustainable and cost-effective option for Imini village. This scenario not only met the community’s average daily demand and AC primary load but also achieved zero CO₂ emissions, unlike the Fossil Fuel Generator (FFG) base. Although some hybrid options offered relatively low Levelized Cost of Energy, they still carried significant emission burdens. By contrast, the WT+SPS+PEMFC mix balanced affordability with environmental sustainability, positioning it as the optimal pathway for rural electrification. This highlights the comparative advantage of integrating renewable sources with fuel cell storage over continued reliance on diesel generators.

COMPETING INTERESTS DISCLAIMER:

Authors have declared that they have no known competing financial interests OR non-financial interests OR personal relationships that could have appeared to influence the work reported in this paper.

Disclaimer (Artificial intelligence)

Option 1:

Author(s) hereby declare that NO generative AI technologies such as Large Language Models (ChatGPT, COPILOT, etc.) and text-to-image generators have been used during the writing or editing of this manuscript.

Option 2:

Author(s) hereby declare that generative AI technologies such as Large Language Models, etc. have been used during the writing or editing of manuscripts. This explanation will include the name, version, model, and source of the generative AI technology and as well as all input prompts provided to the generative AI technology

Details of the AI usage are given below:

1.

2.

3.

References

Adeyemi, A. O. (2013). Electricity consumption and economic growth in Nigeria. Scientific Papers: Journal of Business Management and Applied Economics, 2(4). http://www.scientificpapers.org

Ajayi, O. O. (2009). Assessment of utilization of wind energy resources in Nigeria. Energy Policy, 37, 750–753. https://doi.org/10.1016/j.enpol.2008.10.040

Al Garni, H. Z., Awasthi, A., & Ramli, M. A. (2018). Optimal design and analysis of grid-connected photovoltaic under different tracking systems using HOMER. Energy Conversion and Management, 155, 42–57. https://doi.org/10.1016/j.enconman.2017.10.078

Alliance for Rural Electrification. (2012). Hybrid power systems based on renewable energies: A suitable and cost-competitive solution for rural electrification. http://www.ruralelec.org/fileadmin/DATA/Documents/06_Publications/Position_papers/ARE-WG_Technological_Solutions_-_Brochure_Hybrid_Systems.pdf

Al-Othman, A., Tawalbeh, M., Martis, R., Dhou, S., Orhan, M., Qasim, M., & Olabi, A. G. (2022). Artificial intelligence and numerical models in hybrid renewable energy systems with fuel cells: Advances and prospects. Energy Conversion and Management, 253, 115154. https://doi.org/10.1016/j.enconman.2021.115154

Bertuccioli, L., Chan, A., Hart, D., Lehner, F., Madden, B., & Standen, E. (2014). Study on development of water electrolysis in the EU. Fuel Cells and Hydrogen Joint Undertaking.

Buragohain, S., Mohanty, K., & Mahanta, P. (2021). Hybridization of solar photovoltaic and biogas system: Experimental, economic and environmental analysis. Sustainable Energy Technologies and Assessments, 45, 101050. https://doi.org/10.1016/j.seta.2021.101050

Carmo, M., Fritz, D., Mergel, J., & Stolten, D. (2013). A comprehensive review on PEM water electrolysis. International Journal of Hydrogen Energy, 38(12), 4901–4934. https://doi.org/10.1016/j.ijhydene.2013.01.151

Chedid, R., & Akiki, H. (1998). A decision support technique for the design of hybrid solar-wind power system. IEEE Transactions on Energy Conversion, 13(1), 154–176. https://doi.org/10.1109/60.661634

Chen, L., & Yang, Z. (2012). Design and optimizing a hybrid photocatalytic/electrolytic water-splitting system. Engineering Science Programme, National University of Singapore, Kent Ridge, Singapore.

Council for Renewable Energy, Nigeria (CREN). (2009). Nigeria electricity crunch. www.renewablenigeria.org

Dokua Sasu, D. (2022). Electricity in Nigeria - statistics and facts. Statista. https://www.statista.com/statistics/1234567/electricity-in-nigeria

KPMG. (2022). Power sector update: Edition 2022, Q2. https://home.kpmg/content/dam/kpmg/ng/pdf/power-sector-watch-edition-2022-q2.pdf

Reuters. (2021, August 12). World to reach peak oil demand before 2030. Reuters. https://www.reuters.com/business/energy/world-to-reach-peak-oil-demand-before-2030-2021-08-12/

Rehman, S., & Al-Hadhrami, L. M. (2010). Study of a solar PV-diesel-battery hybrid power system for a remotely located population near Rafha, Saudi Arabia. Energy, 35(11), 4986–4995. https://doi.org/10.1016/j.energy.2010.08.025

Olajide, T. (2020, June 25). See how much Nigeria loses annually to power outages. Financial Watch.

Zubairu, I., Falode, O. A., Diji, C. J., Awonusi, A. A., Afolalu, S. A., Akinlabi, E. T., & Ikumapayi, O. M. (2023). Evaluation of a hybrid solar power system as a potential replacement for urban residential and medical economic activity areas in southern Nigeria. AIMS Energy, 11(2), 319–336.

International Energy Agency (IEA) (2022). Africa Energy Outlook 2022. Paris: IEA.

Otekunrin, O. A., Otekunrin, O. A., Momoh, S., & Ayinde, I. A. (2021). Biomass energy utilization and its relevance for sustainable development in sub-Saharan Africa: A review. Energy Reports, 7, 5022–5036.

Zubairu, I., Falode, O. A., Diji, C. J., Awonusi, A. A., Afolalu, S. A., Akinlabi, E. T., & Ikumapayi, O. M. (2022). A global overview of renewable energy strategies. AIMS Energy, 10(4), 718–775. https://doi.org/10.3934/energy.2022034

Zubairu, I., Falode, O. A., Diji, C. J., Kazeem, R. A., Ikumapayi, O. M., Jen, T.-C., Laseinde, O. T., & Akinlabi, E. T. (2024). Analysis of a hybrid solar power system as a potential substitute in selected Southern Nigerian economic activity areas. In O. T. Laseinde & A. C. Eloka-Eboka (Eds.), Localized energy transition in the 4th industrial revolution (1st ed., pp. 105–119). CRC Press. https://doi.org/10.1201/9781032651958-6

Luo, X., Liu, Y., & Liu, X. (2021). Bi-level multi-objective optimization of design and subsidies for standalone hybrid renewable energy systems: A novel approach based on artificial neural network. Journal of Building Engineering, 41, 102744. https://doi.org/10.1016/j.jobe.2021.102744

Alternative Energy Tutorials. (n.d.). Retrieved July 17, 2025, from http://www.alternative-energy-tutorials.com

Hydrogenics. (n.d.). Hydrogen technology: Electrolysis. Retrieved July 17, 2025, from http://www.hydrogenics.com/technology-resources/hydrogen-technology/electrolysis

How Stuff Works. (n.d.). How solar cells work. Retrieved July 17, 2025, from http://science.howstuffworks.com/environmental/energy/solar-cell3.htm

Renewable Energy Sources. (n.d.). Retrieved July 17, 2025, from http://www.renewable-energysources.com/

Ecology.com. (2011, September 6). Fossil fuels and renewable energy resources. Retrieved July 17, 2025, from http://www.ecology.com/2011/09/06/fossil-fuels-renewable-energy-resources/

Tufts University. (n.d.). Renewable energy economics [PDF]. Retrieved July 17, 2025, from http://www.ase.tufts.edu/gdae/education_materials/modules/RenewableEnergyEcon.pdf

Alternative Energy Tutorials. (n.d.). Retrieved July 17, 2025, from http://www.alternative-energy-tutorials.com