Original Research Article

Correlation Analysis of Wind Speed and Grid Interruption-Induced Outages and Energy Losses in North Central States, Nigeria

ABSTRACT

Despite the widespread use of power in Nigeria, the electricity supply suffer power deficit, poor quality and sporadic supply especially in the North Central States. Most overhead transmission lines are exposed to natural phenomena especially strong wind which can cause vibration in the conductors and cause the conductors to become closer to or separate away from the body of the tower leading to power outage. This study examined the effect of wind speed on grid interruption and outages in North Central States of Nigeria using correlation analysis of three years NASA wind speed data obtained from NASA/POWER CERES/MERRA2 (2020-2022) and utility outage records. Result shows that, wind speed is observed to be stronger in January, February, August and December throughout the three years period especially January and December. For wind speed at 10m, the total load losses were 121.15MW, 789.5MW and 58.5MW which amounted to energy losses 431.7MWH, 2203.8MWH and 216.8MWH in 2020, 2021 and 2022 respectively. Similarly, for wind speed at 50m, the total load losses were 169.68MW, 1689.17MW and 80.2MW with corresponding energy losses 604.38MWH, 4715.66MWH and 325.21MWH respectively. Out of the total energy losses, wind speed at 10m contributed 46.4%, 25.9% and 29.4%, while wind speed at 50m contributed 64.9%, 54.9% and 50.0% in 2020, 2021 and 2022 respectively. Also, wind speed at 50m range has highest speed across the 3 years. This implies that wind at 50m is a more significant factor for outages than wind at 10m, regression coefficient R2 = 0.121 against 0.050 and unstandardized beta coefficient β = 0.348 against –0.223 at 95% CI, suggesting issues with taller structures or vegetation contact. The findings of this study are relevant for power grid operators, policymakers, and infrastructure planners in Nigeria, highlight the importance of improving power infrastructure, regular scheduled maintenance most especially at the beginning of the year when wind speed is high in North Central States of Nigeria.

Keywords:  Grid interruption, load loss, wind speed, power outage, energy loss, north central Nigeria.

1. INTRODUCTION

The epileptic power supply has adversely affected the growth rate of Nigeria. According to the National Bureau of Statistics, Nigeria is the most populated country in Africa and the seventh most populated in the world, with a population estimate of 208 million people [1]. Population, among other variables such as the gross domestic product, relates to electricity consumption (Kavaklioglu, 2019; To et al., 2017), the demand for power supply is expected to be high, and thus the power generated. Electricity supply has revolutionized how people communicate, conduct business and access information. Nigeria, being one of the largest markets in Africa, has seen relative growth in industrialization. However, Oloniniran (2022) reported that the National Grid system has collapsed for the seventh time in the year, resulting in a complete blackout in many places. Poor electricity supply discourages international investors from investing in the country. In 2023, about 61% of Nigerians had access to electricity, a gradual improvement from earlier years, yet the country still faced the largest electricity access deficit globally, with roughly 86 million people lacking reliable power (Guardian Nigeria, 2025; Sasu, 2025). Though, generation has increased, by 14.09% year-on-year to 5,731.60 GWh in Q3 2023, it is insufficient to meet the demand and address the large deficit. Total number of electricity customers continues to grow, reaching 12.33 million in Q1 2024. Presently, Nigeria has twenty-three (23) power-generating plants connected to the national grid with the capacity to generate 11,165.4 MW of electricity, very much less than the 40,000 MW needed to sustain the basic needs of the population (Akanji, 2016; NERC, 2025).

North-Central States of Nigeria, reflect the broader national trend of increasing reliance on power supply due to its diverse geographical landscape, comprising urban centers, rural communities, and remote areas (Olaniyan et al., 2018). Despite the widespread use electricity, the quality of service particularly acceptable voltage, remains inconsistent across different parts of the area. Factors such as infrastructural and operational challenges contribute to poor quality of supply (Nemeth-Durko et al., 2020; Ezenugu et al., 2017; Oyedepo, 2019). The transmission and distribution industry is responsible for power supply in North Central States of Nigeria. This industry have made significant investments in infrastructure, particularly in urban areas-Abuja, however, residents in more rural or remote areas often face challenges related to poor voltage, prolonged outages, and limited access to power supply (Murray & Adonis, 2019; Murray, 2018; Tukur & Solomon, 2019). Most overhead transmission lines are exposed to natural phenomena especially strong wind, high temperature and heavy rain which directly or indirectly leads to a change in the clearances and geometry of tower tops cause vibration in the conductors leading to power outages, operational challenges, high technical and commercial losses. Therefore, this study seeks to address the problem by analyzing the wind speed that causes tripping and outages in North Central States of Nigeria. The results of this study will provide valuable information for power industry, policymakers, and other stakeholders working to improve power supply in North Central States of Nigeria.

2. MATERIALS AND METHODS

2.1 Materials

The main material used are data which covers a period of 3 years, between Jan, 2020 to Dec, 2022 is used. Obtained from NASA/POWER CERES/MERRA2 Native Resolution Monthly and Annual Latitude and Longitude of North Central States of Nigeria. Elevation from MERRA-2, Proteus software, Electronics Workbench, Laptop (computer) and network signal info.

2.2 Methods

2.2.1 Research Design

To obtain representative samples for the study, a purposive sampling technique was used to randomly sample the feeders in North Central States. Seven (7) outgoing feeders from Seven States were used for this study. The method adopted for the Simulation of IoT Wind speed Transmission Line Fault Control and Monitoring System is in three parts including software design which involves simulation and testing of the circuit, employing secondary data and comparing the simulated result with that of secondary data in order to ensure its proper functionality, and relating the secondary result with that of substation to come up with a wind speed model. The methodology adopted by this study was a 4-tier approach viz; Data collection, profiling, synthesis, modeling and analysis with a focus to determine the effects of wind speed on Grid interruption and outages.

2.2.2 The Study Area

The study involves the six North Central States of Nigeria and the Federal Capital Territory (FCT} located on latitude 6°431N and 6°451N and longitude 6°601E and 6°801E with a geographical coverage of 242,425 km2 (Adaramola, 2014). Tripping data of the stations were collected from all these States and the feeder locations, identification codes and GPS locations of all the states are presented in Table 1, while the map of North Central showing the feeder locations is shown in Figure 1.

Table 1: Identification Codes and GPS Location of North Central States of Nigeria

| Study Location | Code ID | Latitude | Longitude | Altitude (m) |
| --- | --- | --- | --- | --- |
| Abuja Feeder | ABF | 9.0563° N | 7.4985° E | 400.00 |
| Plateau Feeder | PLF | 9.2182° N | 9.5179° E | 1200.00 |
| Kwara Feeder | KWF | 8.9669° N | 4.3874°.E | 286.86 |
| Nasarawa Feeder | NAF | 8.4998° N | 8.1997° E | 400.00 |
| Niger Feeder | NIF | 9.9309° N | 5.5983° E | 200.00 |
| Kogi Feeder | KGF | 7.7337° N | 6.6906 E | 125.00 |
| Benue Feeder | BEF | 7.3369° N | 8.7404° E. | 250.00 |

Figure 1: Map of North Central States of Nigeria showing feeder locations

2.2.3 Method of Data Analysis

Total Energy Loss: The total energy loss due to the effect of wind speed on the grid is expressed as follows:

Energy Loss (E) = Average Load Lost (P) × Outage Duration (T)					(1)

where P is the amount of load that was out of service for the duration T.

The Load lost (P) can be expressed as the load before the outage occurs i.e. the power being delivered to the end-user(s) or the load served by the affected transmission line. This is typically given by:

Power (P) = V × I × cos(θ)									(2)

where V is the voltage, I is the current, and cos(θ) is the power factor of the load. For a typical transmission line with substation to load distance L in km, this is the same as:

(3)

where Ploss is the line losses (W), R is the line resistance (Ω), L is the substation to load distance in km, IL is the line current (A).

Additionally, the total load lost can be considered as Power Shortage (ES(t)) at a given time t, and the total energy lost over a period is the sum of these power shortages multiplied by their respective durations given as:

Energy Loss E=i=1nESti								(4)

where ES is power shortage and ti is the outage durations for times i = 1, 2, 3, ….., n.

Model 1: Effect of Wind Speed at 10m on Power Outages

A simple linear regression model was specified as:

Yit=α+βX10m, it+εit 									(5)

where Yit is the number of power outages in month t of year I, X10m, it is the mean wind speed at 10 meters, α is a constant (intercept), β is the regression coefficient showing the effect of wind speed at 10m on outages, and εit is the error term.

Hypothesis I:

- H0: Wind speed at 10m has no significant effect on power outages (β = 0).

- H1: Wind speed at 10m significantly affects power outages (β ≠ 0).

Model 2: Effect of Wind Speed at 50m on Power Outages

A simple linear regression model was specified as:

Yit=α+βX50m, it+εit 									(4)

Yit is the number of power outages in month t of year I, X50m, it is the mean wind speed at 50 meters, α is a constant (intercept), β is the regression coefficient showing the effect of wind speed at 50m on outages, and εit is the error term.

Hypothesis II:

- H0: Wind speed at 50m has no significant effect on power outages (β = 0).

- H1: Wind speed at 50m significantly affects power outages (β ≠ 0).

3 RESULTS

The result of the mean wind speed at 10m and 50m Range from the seven states for the period of three years (2020 - 2022) are presented in Tables 2 and 3. While the result of the power outage, load loss and energy loss for wind speed at 10m and 50m for the corresponding periods are presented in Table 4 and 5 respectively..

Table 2: Mean wind speed at 10m range

| S/N | Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Ann |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 2020 | 9.59 | 7.36 | 4.97 | 7.87 | 5.21 | 4.81 | 5.95 | 7.23 | 6.49 | 5.62 | 6.67 | 6.19 | 9.66 |
| 2 | 2021 | 6.66 | 8.93 | 6.98 | 7.02 | 6.09 | 4.84 | 5.58 | 6.73 | 6.45 | 5.55 | 4.81 | 6.23 | 8.94 |
| 3 | 2022 | 7.09 | 6.90 | 6.31 | 5.03 | 4.46 | 4.95 | 4.39 | 7.47 | 5.30 | 5.84 | 6.33 | 6.32 | 7.51 |

Table 3: Mean wind speed at 50m range

| S/N | Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Ann |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 2020 | 12.07 | 11.50 | 8.84 | 10.05 | 6.40 | 6.38 | 7.34 | 9.05 | 7.73 | 7.77 | 9.09 | 9.60 | 12.10 |
| 2 | 2021 | 10.37 | 11.66 | 9.62 | 9.46 | 7.17 | 5.80 | 6.87 | 8.28 | 7.59 | 6.77 | 8.61 | 9.48 | 11.91 |
| 3 | 2022 | 10.92 | 10.62 | 10.19 | 6.52 | 5.66 | 5.88 | 5.85 | 9.29 | 6.32 | 8.34 | 10.27 | 10.48 | 11.21 |

Figure 2. Wind speed at 10m range from 2020 to 2022

Figure 3. Wind speed at 50m range from 2020 to 2022

Figure 2 shows the wind speed at 10m range from 2020 to 2022. In 2020, the wind speed was very high in January, moderate in February, April, August, September and November, while it was low in March, May and June. In the 2021, the wind speed was very high in February, the moderate almost throughout the year except in June and November where it was very low. In 2022 the wind speed was just moderate but low from April to July. Annual wind speed was order is 2020>2021>2022 respectively. This implies that tripping and outages can be observed more frequent from January to April due to strong wind during this period and to maintain power supply, fault clearing must be done regularly within such periods.

Figure 3 also shows a wind speed at 50m range from 2020 to 2022. In 2020, the wind speed was very high in January and February, it was the moderate throughout except for May and June where it was low. In 2021, the wind speed was also high in January and February and then low in May, June July and October. In 2022, the wind speed become very high in January, February, November and December, then moderate in August and October and low in other months. The order of annual wind speed is also 2020>2021>2022. However, comparing wind speed at 10m and 50m range, we see that 50m has higher speed of 12.07 in Jan 2020 than 9.59 of 10m range in the same year. Its least 5.85 in July 2022 is also higher than 4.39 of 10m range in 2022 also. Both recorded low speed in May, June and July all round. Annual record shows that 50m range has highest speed across the 3 years than those of 10m range.

Table 4: Analysis of mean wind speed, outages, load loss and energy loss at 10m range

| Year | Year 2020 |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Months | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |
| Mean Wind Speed (m/s) | 9.59 | 7.36 | 4.97 | 7.87 | 5.21 | 4.81 | 5.95 | 7.23 | 6.49 | 5.62 | 6.67 | 6.19 |
| Number of Outages | 25 | 15 | 8 | 6 | 3 | 7 | 1 | 7 | 4 | 4 | 4 | 13 |
| Load Loss (MW) | 67.30 | 40.40 | 21.50 | 16.20 | 8.10 | 18.85 | 2.69 | 18.85 | 10.80 | 10.8 | 10.80 | 35.00 |
| Energy Loss (MWH) | 239.8 | 143.9 | 76.7 | 57.56 | 28.8 | 67.2 | 9.59 | 67.2 | 38.37 | 38.37 | 38.37 | 124.7 |
|  | Year 2021 |  |  |  |  |  |  |  |  |  |  |  |
| Mean Wind Speed (m/s) | 6.66 | 8.93 | 6.98 | 7.02 | 6.09 | 4.84 | 5.58 | 6.73 | 6.45 | 5.55 | 4.81 | 6.23 |
| Number of Outages | 6 | 11 | 16 | 18 | 35 | 22 | 20 | 21 | 15 | 14 | 12 | 3 |
| Load Loss (MW) | 94.70 | 173.7 | 252.6 | 284.2 | 553 | 347.4 | 315.8 | 331.6 | 236.8 | 221.1 | 189.5 | 47.40 |
| Energy Loss (MWH) | 264.5 | 484.9 | 705.3 | 793.2 | 1542.8 | 969.8 | 881.6 | 925.7 | 661.2 | 617.1 | 528.9 | 132.2 |
|  | Year 2022 |  |  |  |  |  |  |  |  |  |  |  |
| Mean Wind Speed (m/s) | 7.09 | 6.90 | 6.31 | 5.03 | 4.46 | 4.95 | 4.39 | 7.47 | 5.30 | 5.84 | 6.33 | 6.32 |
| Number of Outages | 10 | 4 | 2 | 1 | 6 | 2 | 2 | 1 | 1 | 2 | 2 | 1 |
| Load Loss (MW) | 53.5 | 21.4 | 10.7 | 5.35 | 32.10 | 10.70 | 10.70 | 5.35 | 5.35 | 10.7 | 10.7 | 5.35 |
| Energy Loss (MWH) | 216.8 | 86.73 | 43.4 | 21.68 | 130.1 | 43.41 | 43.4 | 21.68 | 21.68 | 43.40 | 43.40 | 21.68 |

Figure 4. Mean wind speed vs outages, load loss and energy loss at 10m range for 2020

Figure 5. Mean wind speed vs outages, load loss and energy loss at 10m range for 2021

Figure 6. Mean wind speed vs outages, load loss and energy loss at 10m range for 2022

Table 5: Analysis of mean wind speed, outages, load loss and energy loss at 50m range

| Year | Year 2020 |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Months | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |
| Mean Wind Speed (m/s) | 12.07 | 11.50 | 8.84 | 10.05 | 6.40 | 6.38 | 7.34 | 9.05 | 7.73 | 7.77 | 9.09 | 9.60 |
| Number of Outages | 14 | 15 | 6 | 9 | 3 | 1 | 1 | 7 | 4 | 5 | 7 | 25 |
| Load Loss (MW) | 37.71 | 40.4 | 16.16 | 24.24 | 8.08 | 2.69 | 2.69 | 18.85 | 10.77 | 13.47 | 18.85 | 67.34 |
| Energy Loss (MWH) | 134.31 | 143.90 | 57.56 | 86.34 | 28.78 | 9.59 | 9.59 | 67.15 | 38.37 | 47.97 | 67.15 | 239.84 |
|  | Year 2021 |  |  |  |  |  |  |  |  |  |  |  |
| Mean Wind Speed (m/s) | 10.37 | 11.66 | 9.62 | 9.46 | 7.17 | 5.80 | 6.87 | 8.28 | 7.59 | 6.77 | 8.61 | 9.48 |
| Number of Outages | 22 | 35 | 18 | 11 | 7 | 3 | 15 | 21 | 20 | 14 | 13 | 16 |
| Load Loss (MW) | 347.39 | 552.67 | 284.23 | 173.7 | 110.5 | 47.37 | 236.86 | 331.18 | 315.81 | 221.07 | 205.27 | 252.65 |
| Energy Loss (MWH) | 969.79 | 1541.8 | 793.46 | 484.89 | 308.57 | 132.24 | 661.22 | 925.71 | 881.63 | 617.14 | 573.06 | 705.30 |
|  | Year 2022 |  |  |  |  |  |  |  |  |  |  |  |
| Mean Wind Speed (m/s) | 10.92 | 10.62 | 10.19 | 6.52 | 5.66 | 5.88 | 5.85 | 9.29 | 6.32 | 8.34 | 10.27 | 10.48 |
| Number of Outages | 11 | 4 | 3 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 1 | 6 |
| Load Loss (MW) | 51.96 | 18.89 | 14.17 | 4.72 | 4.72 | 4.72 | 4.72 | 9.45 | 4.72 | 9.45 | 4.72 | 28.30 |
| Energy Loss (MWH) | 210.43 | 76.52 | 57.39 | 19.13 | 19.13 | 19.13 | 19.13 | 38.26 | 19.13 | 38.26 | 19.13 | 114.78 |

Figure 7. Mean wind speed vs outages, load loss and energy loss at 50m range for 2020

Figure 8. Mean wind speed vs outages, load loss and energy loss at 50m range for 2021

Figure 9. Mean wind speed vs outages, load loss and energy loss at 50m range for 2022

Figures 4, 5 and 6 presents the analysis for wind speed on outages at 10m for years 2020, 2021 and 2022 respectively. In 2020, the wind speed did not show much effect on outages all year round, it was only effective in January August, and December as revealed by the trend in Figure 4, leading to load losses of 67.30MW, 18.85MW and 35.00MW respectively. These losses corresponds to energy losses of 239.8MWH, 67.2MWH and 124.7MWH respectively. In 2021, the wind speed was only effective in February, April and August as shown in Figure 5. These translates to load losses of 173.7MW, 284.2MW and 331.6MW, corresponding to energy losses of 484.9MWH, 793.2MWH and 925.7MWH respectively. In 2022, the wind speed was only effective to cause outages in January (Figure 6) with a load loss of 58.5MW and energy loss of 216.8MWH. This implies that the wind speed did not have much effect on outages at 10m suggesting that most of the outages experienced were due to other factors like rain, high temperature and equipment failures. In general, the wind speed at 10m contributed to a total load losses of 121.15MW, 789.5MW and 58.5MW and energy losses of 431.7MWH, 2203.8MWH and 216.8MWH in year 2020, 2021 and 2022 respectively.

Figures 7, 8 and 9 presents the analysis for wind speed on outages at 50m for years 2020, 2021 and 2022 respectively. The trend in the graphs have revealed significant information that is worth interpreting. The wind speed causes outages all year round in 2020, 2021 and 2022. These is evident from the trend in the graph as high wind speeds corresponds to high outages, while low wind speed corresponds to low outages. It implies that wind speed at 50m is significant to cause outages. In 2020, peak values are observed in February, April, August, November and December as shown in Figure 7. These translates to load losses of 40.4MW, 24.24MW, 18.85MW, 18.85MW and 67.34MW, corresponding to energy losses of 143.90MWH, 86.34MWH, 67.15MWH, 67.15MWH, and 239.84MWH respectively. In 2021, peak values are observed in February, July, August, September, and December as shown in Figure 8. There translates to load losses of 552.67MW, 236.86MW, 331.18MW, 315.81MW, and 252.65MW, corresponding to energy losses of 1541.8MWH, 661.22MWH, 925.71MWH, 881.63MWH, and 705.30MWH respectively. In 2022, the peak values were observes in January and December as shown in Figure 9. There translates to load losses of 51.96MW and 28.30MW, corresponding to energy losses of 210.43MWH and 114.78MWH respectively. In general, the wind speed at 50m contributed to a total load losses of 169.68MW, 1689.17MW and 80.2MW and energy losses of 604.38MWH, 4715.66MWH and 325.21MWH in the year 2020, 2021 and 2022 respectively.

To further confirm this effect, a simple linear regression was conducted to examine whether wind speed at 10m and 50m significantly predicts power outages from 2020 to 2022. The result of the analysis is presented in Table 6.

Table 6: Simple regression analysis on No significant effect of wind speed at 10m and 50m on power outages from 2020 to 2022

| DV | Predator | R | R2 | F | df | 95%CI | β | t | p |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Power Outages | Wind Speed at 10m | 0.223 | 0.050 | 16.877 | 1,324 | [-1.920, -0.677] | -0.223 | -4.108 | 0.000 |
| Power Outages | Wind Speed at 50m | 0.348 | 0.121 | 44.544 | 1,332 | [0.907, 1.666] | 0.348 | 6.674 | 0.000 |

From Table 6, the analysis revealed a statistically significant negative relationship between wind speed at 10m and power outages, R = 0.223, R² = 0.050, F(1,324) = 16.88, p < 0.001. This indicates that approximately 5.0% of the variance in power outages can be explained by wind speed at 10m. The regression coefficient was negative and significant (β = –0.223, 95% CI [–1.920, –0.677]), suggesting that as wind speed at 10m increases, the occurrence of power outages tends to decrease. Given the p-value of 0.000 (p < 0.001), the null hypothesis of no significant effect was rejected. The results indicate that wind speed measured at 10m has a significant negative effect on power outages. This means that higher wind speeds at this altitude are associated with fewer power outages during the study period. With 5% of the variance in power outages explained by wind speed at 10m, further confirms that most of the outages experienced were due to other factors like rain, high temperature and equipment failures rather than wind speed at 10m.

The results from Table 6 also showed that wind speed at 50m was a significant positive predictor of power outages, R = 0.348, R² = 0.121, F(1,332) = 44.544, p < 0.001. This indicates that approximately 12.1% of the variance in power outages can be explained by wind speed at 50m. The unstandardized beta coefficient (β = 0.348, 95% CI [0.907, 1.666]) suggests that for every one-unit increase in wind speed at 50m, there was a corresponding increase in power outages. Given that p < 0.001, the null hypothesis of no significant effect was rejected, confirming that higher wind speeds at 50m are associated with a greater likelihood of power outages. The findings of this study demonstrate that wind speed at 50m has a significant positive effect on power outages between 2020 and 2022. With an R² value of 0.121, the model indicates that approximately 12.1% of the variance in power outages can be explained by changes in wind speed at 50m. The positive beta coefficient (β = 0.348) suggests that as wind speed at 50m increases, the likelihood of power outages also rises. Given that the relationship was statistically significant (p < 0.001), the null hypothesis of no significant effect was rejected.

4. DISCUSSION

This study reveals the effect of wind speed at 10m and 50m on the grid interruption and outages in North Central States of Nigeria during the year 2020 to 2022. The result from the analysis have revealed valuable information showing variation in trend across the years. Findings have revealed that the wind speed at 10m did not have much effect on grid interruption as compared to the wind speed at 50m. As such, the load loss and energy losses for the 10m wind speed were less compared to the 50m wind speed. Wind speed are observed to be stronger in January, February, August and December throughout the three years period especially January and December. Findings have shown that at 10m wind speed the total load loss experienced was 121.15MW, 789.5MW and 58.5MW, which corresponds to total energy losses of 431.7MWH, 2203.8MWH and 216.8MWH in year 2020, 2021 and 2022 respectively. While for the 50m wind speed the total load losses were 169.68MW, 1689.17MW and 80.2MW, which corresponds to total energy losses of 604.38MWH, 4,715.66MWH and 325.21MWH in the year 2020, 2021 and 2022 respectively. This finding is similar to that of Onyishi and Ejofodomi (2021) who found total energy loss of 230.1MWH on distribution lines in Ebonyi State, Nigeria. However, this finding is not in line with that of Akanni et al. (2023) who found a total energy loss of 15,754.80MWH due to outages in the distribution system in Lagos State, Nigeria.

Energy loss for the 10m wind speed and 50m wind speed showed same patter and the order of energy loss for the three years analysis is 2021 > 2020 > 2022. However, wind speed at 10m contributed 46.4%, 25.9% and 29.4% out of the total energy losses, while wind speed at 50m contributed 64.9%, 54.9% and 50.0% in 2020, 2021 and 2022 respectively. This suggest that even though the amount of energy loss was higher in 2021, the percentage due to wind effect was rather higher in 2020 as compared to other years for both 10m and 5m wind speed. Losses occurred due to transient fault, which are caused by lightning, line switching, swinging wires due to strong wind and other weather conditions, weak and inadequate network coverage, and substandard transmission and distribution lines like weak or faulty jumper cuts. This finding is in line with that of Etukudor et al. (2015), Akanni et al. (2023), and Akintola and Awosope (2017).

5. CONCLUSION

The findings of this study provide valuable insights into the wind speed and outage profile for North Central States. The analysis revealed significant differences in weather conditions at every month of the year and the effect on the power transmission and distribution network as more tripping occurs at between January and March due to strong winds which occur at that period, if there is not regular tree trimming, line and equipment maintenance, outages will be recorded. This implies that wind speed is an important environmental factor influencing the stability of the power supply and should be considered in planning and implementing strategies for power infrastructure resilience. It underscores the importance of strategic placement of transmitting and distribution stations to improve power supply with good quality, especially in areas with poor quality like urban and sub urban locations within the North Central State. The findings of this study highlight the potential importance of considering wind patterns at higher elevations when developing strategies to improve the stability and resilience of power infrastructure. Also, it is recommended that the power Industry should invest in improving their infrastructure and maintenance. Finally, collaboration between power industry and government agencies can help improve power supply.

COMPETING INTERESTS DISCLAIMER:

Authors have declared that they have no known competing financial interests OR non-financial interests OR personal relationships that could have appeared to influence the work reported in this paper.

Disclaimer (Artificial intelligence)

Option 1:

Author(s) hereby declare that NO generative AI technologies such as Large Language Models (ChatGPT, COPILOT, etc.) and text-to-image generators have been used during the writing or editing of this manuscript.

REFERENCES

Adaramola, M. S. (2014). Viability of grid-connected solar PV energy system in Jos, Nigeria. International Journal of Electrical Power & Energy Systems, 61(1), 64-69.

Akanji, A.A. (2016). Spatial exploration and analysis of electricity poverty: a case study of Ibadan, Southwestern, Nigeria (PhD Thesis). Department of Geography. University of Leicester.

Akanni, S. A., Melodi, A. O. & Ale, T. O. (2023). Analysis of the causes of outages in the distribution system of Lagos State, Nigeria. FUOYE Journal of Engineering and Technology, 8(1), 53-57.

Akintola, A. & Awosope, C. (2017). Reliability analysis of secondary distribution system in Nigeria: A case study of Ayetoro I Substation, Lagos State. The International Journal of Engineering and Science, 6(7), 13-21.

Alao, A. A. (2016). Residential and Industrial Electricity Consumption Dynamics and Economic Growth in Nigeria 1980-2010. International Journal of Economy, Energy and Environment, 1(3), 55-63.

Ayadi, O., Al-Assad, R. & Al Asfar, J. (2018). Techno-economic assessment of a grid connected photovoltaic system for the University of Jordan. Sustainable Cities and Society, 39, 93-98.

Azerefegn, T. M., Bhandari, R. & Ramayya, A. V. (2020). Techno-economic analysis of grid-integrated PV/wind systems for electricity reliability enhancement in Ethiopian industrial park. Sustainable Cities and Society, 53, 1-32.

Azodo, A. P. (2014). Electric power supply, main source and backing: A survey of residential utilization features. International Journal of Research Studies in Management, 3(2), 87-102.

Babatunde, M. A. & Shuaibu, M. I. (2009). The demand for residential electricity in Nigeria: a bound testing approach. In Proceedings of 2nd International Workshop on Empirical Methods in Energy Economics, Zurich, Switzerland, 1-16.

Emovon, I., Samuel, O. D., Mgbemena, C. O. & Adeyeri, M. K. (2018). Electric Power generation crisis in Nigeria: A Review of causes and solutions. International Journal of Integrated Engineering, 10(1), 45-56.

Etukudor, C., Abdulkareem, A. & Ayo, O. (2015). The daunting challenges of the Nigerian electricity supply industry. Journal of Energy Technologies and policy, 5(9), 25-32.

Ezenugu, I. A., Nwokonko, S. C. & Markson, I. (2017). Modelling and Forecasting of residential electricity consumption in Nigeria using Multiple and Quadratic regression models. American Journal of Software Engineering and Applications, 6(3), 99-104.

Guardian Nigeria (26 Jun 2025). Nigeria tops global list for lack of electricity access. Accessed on 21th august, 2025. Available at https://guardian.ng/news/nigeria-tops-global-list-for-lack-of-electricity-access/#google_vignette.

Idowu, S. S., Ibietan, J. & Olukotun, A. (2019). Nigeria’s Electricity Power Sector Reform: An Appraisal of Unresolved Issues. International Journal of Energy Economics and Policy, 9(6), 336-341.

Kavaklioglu, K. (2019). Principal components based robust vector autoregression prediction of Turkey’s electricity consumption. Energy Systems, 10(4), 889-910.

Murray, W. & Adonis, M. (2019). Efficacy of Energy Wheeling to Endorse Renewable Energy Generation. Paper presented at the AIUE Proceedings of the 17th Industrial and Commercial Use of Energy (ICUE) Conference, Cape Town, 1-8.

Murray, W. N. (2018). Energy wheeling viability of distributed renewable energy for industry (Master of Engineering), Cape Peninsula University of Technology.

Nazir, R., Laksono, H.D., Waldi, E.P., Ekaputra, E. & Coveria, P. (2014). Renewable Energy Sources Optimization: A Micro-Grid Model Design. In Proceedings of the International Conference on Alternative Energy in Developing Countries and Emerging Economies, 2013, Bangkok, Thailand. 52 (1), 316-327. DOI: 10.1016/j.egypro.2014.07.083.

Nemeth-Durko, E., Juhasz, P. & Dudas, F. (2020). Forecasting residential electricity consumption based on urbanization and income projections. Paper presented at the ECMS, 104-110.

NERC (2025). NERC first quarter 2025 report. Nigerian electricity regulatory commission. Accessed on 24th August, 2025. Available at https://nerc.gov.ng/resource-category/nerc-reports/

Olaniyan, K., McLellan, B., Ogata, S. & Tezuka, T. (2018). Estimating residential electricity consumption in Nigeria to support energy transitions. Sustainability, 10(1440), 1-22.

Olanrewaju, S., Olafioye, S. & Oguntade, E. (2020). Modelling Nigeria Population Growth: A Trend Analysis Approach. International Journal of Innovative Science and Research Technology, 5(4), 52-64.

Olaoye, T., Ajilore, T., Akinluwade, K., Omole, F. & Adetunji, A. (2016). Energy crisis in Nigeria: Need for renewable energy mix. American Journal of Electrical and Electronic Engineering, 4(1), 1-8.

Onyishi, D. U. & Ejofodomi O. (2021). The effect of transmission and distribution losses on daily electricity supply in Ebonyi State, Nigeria. Tropical Journal of Science and Technology, 2(1), 60-68. DOI: 10.47524/tjst.21.8.

Oyedepo, S. O. (2019). Energy Use and Energy Saving Potentials in Food Processing and Packaging: Case Study of Nigerian Industries in Bottled and Packaged Water (pp. 423-452): Wood head Publishing.

Sasu, D.D. (Jul 30, 2025). Share of the population with access to electricity in Nigeria 1990-2023.  Message posted to “Statista”. Accessed on 21th august, 2025. Available at https://www.statista.com/statistics/1307416/total-population-access-to-electricity-in-nigeria/.

Taale, F. & Kyeremeh, C. (2019). Drivers of households’ electricity expenditure in Ghana. Energy and Buildings, 205(8), 546-552.

To, W.M., Lee, P.K. C. & Lai, T.M. (2017). Modeling of monthly residential and commercial electricity consumption using nonlinear seasonal models: The case of Hong Kong. Energies, 10(7), 885.

Tukur, M.U. & Solomon, O.I. (2019). Impact of Deregulation on Residential Electricity Consumption in Nigeria: 1980-2017. International Journal of Academic Research in Business and Social Sciences, 9(6), 163-184.