Review Form 3

	

	Journal Name:
	Journal of Engineering Research and Reports 

	Manuscript Number:
	Ms_JERR_148992

	Title of the Manuscript: 
	Power Quality Assessment of Residential Electric Bulbs and Their Harmonic Impacts in Power Systems

	Type of the Article
	


	PART  1: Comments



	
	Reviewer’s comment

Artificial Intelligence (AI) generated or assisted review comments are strictly prohibited during peer review.

	Author’s Feedback (It is mandatory that authors should write his/her feedback here)



	Please write a few sentences regarding the importance of this manuscript for the scientific community. A minimum of 3-4 sentences may be required for this part.


	This manuscript addresses an important and practical issue in modern power distribution systems—harmonic pollution caused by non-linear lighting loads, particularly LED and CFL lamps. With increasing global emphasis on energy-efficient lighting, understanding the harmonic behavior of these devices is crucial for utility providers and electrical engineers. The study provides experimental data that can support power-quality management and awareness in developing regions. The work is beneficial for researchers, distribution companies, and consumers seeking to understand the trade-off between energy efficiency and power quality.
	

	Is the title of the article suitable?

(If not please suggest an alternative title)


	Yes, the title is suitable.
It clearly reflects the content and scope of the study.
	

	Is the abstract of the article comprehensive? Do you suggest the addition (or deletion) of some points in this section? Please write your suggestions here.


	The abstract provides a general overview and correctly identifies the problem, methodology, and major findings.
However, improvements suggested:
· Include quantitative values of harmonic distortion (e.g., LED THD = 145%).

· Avoid repetitive wording.

· Add a more explicit conclusion linking the results to system-level implications.
	

	Is the manuscript scientifically, correct? Please write here.
	The manuscript is largely correct and technically sound. The classification of lamp types, harmonic explanation, and interpretation of waveforms are accurate.
However:
· Some methodological details (exact setup specifications, sampling rate, power meter configuration) could be expanded.

· Many figures are referenced but not visible or low resolution—this must be corrected.

· Quantitative analysis could be strengthened with comparative tables rather than only figures.
	

	Are the references sufficient and recent? If you have suggestions of additional references, please mention them in the review form.
	References are relevant but mostly old (2003–2015).
The manuscript lacks citations after 2018, despite many newer studies on LED harmonic emissions.
Suggested additional recent references:
· IEEE papers on LED driver harmonics (2019–2023).

· IEC standards on harmonic limits (IEC 61000-3-2).
Updating 3–5 references will significantly strengthen the paper.
	

	Is the language/English quality of the article suitable for scholarly communications?


	The language is understandable but requires moderate editing for grammar, clarity, and consistency.
Examples: missing articles, run-on sentences, spacing errors, and inconsistent capitalization.
	

	Optional/General comments


	  Figures must be replaced with clear, high-resolution images.

  Add a summary table comparing all bulbs in terms of THD, PF, harmonic orders, and power rating.

  Discussion should link results to distribution network problems (transformer loading, neutral current, voltage distortion).

  Conclusion should explicitly state the limitations and scope for future work.
The manuscript is technically sound and experimentally supported. The work adds practical value for power-quality assessment in developing countries. Revisions will improve clarity, readability, and technical depth.


	


	PART  2: 



	
	Reviewer’s comment
	Author’s Feedback (It is mandatory that authors should write his/her feedback here)



	Are there ethical issues in this manuscript? 


	(If yes, Kindly please write down the ethical issues here in detail)

No
	


Reviewer details:

Rahul Argelwar, Rashtrasant Tukadoji Maharaj Nagpur University, India

Created by: DR
              Checked by: PM                                           Approved by: MBM
   
Version: 3 (07-07-2024)

