# A Comprehensive Review of Advances and Challenges in Sacrificial Anode Cathodic Protection Systems for Storage Tanks

## Abstract

This comprehensive review examines the current state and future prospects of sacrificial anode cathodic protection (CP) systems for aboveground storage tanks (ASTs). The paper synthesizes recent technological advances in anode materials, system design, and monitoring capabilities while addressing persistent challenges including inconsistent protection coverage, limited service life, and environmental compatibility issues. Key innovations discussed include novel anode alloys, smart monitoring systems integrated with IoT technologies, and hybrid CP configurations. The review identifies controlled potential applications as a promising direction for enhancing system performance and reliability. Through analysis of case studies and industrial applications, this work highlights the transition from traditional sacrificial anode systems toward more sophisticated controlled potential approaches. The findings indicate that while significant progress has been made in materials science and monitoring technologies, substantial research gaps remain in predictive modeling, long-term performance optimization, and standardization of controlled potential systems. This review provides strategic insights for researchers, engineers, and industry practitioners working toward more effective and sustainable corrosion protection solutions for critical infrastructure.

## Keywords: Cathodic Protection (CP), Sacrificial Anode, Aboveground Storage Tanks (ASTs), Electrochemical Protection, Smart Monitoring, IoT Integration,

# Introduction

Aboveground storage tanks (ASTs) represent critical infrastructure components in the oil, gas, chemical, and water treatment industries, serving as essential repositories for valuable resources and potentially hazardous materials [1]. The structural integrity and operational safety of these facilities depend fundamentally on effective corrosion prevention and control strategies. Among the various corrosion protection methods available, cathodic protection (CP) systems have emerged as one of the most widely adopted and effective approaches for mitigating electrochemical deterioration in metallic structures. Corrosion-related failures in ASTs can result in catastrophic consequences, including environmental contamination, economic losses, operational disruptions, and safety hazards, with the annual global cost of corrosion estimated to exceed $2.5 trillion, storage tank failures contributing significantly to this figure[2]. Traditional corrosion prevention methods, while effective in specific applications, often fall short of providing comprehensive, long-term protection for complex storage tank configurations exposed to diverse environmental conditions[3].

Sacrificial anode cathodic protection systems have historically served as the backbone of electrochemical corrosion prevention for ASTs, operating on the principle of galvanic coupling, where more electronegative materials (anodes) preferentially corrode to protect the primary structure (cathode). The inherent simplicity, cost-effectiveness, and passive operation of sacrificial anode systems have made them particularly attractive for industrial applications [4]. However, evolving operational requirements, environmental regulations, and technological capabilities have highlighted significant limitations in conventional sacrificial anode approaches. Contemporary challenges in sacrificial anode CP systems include inconsistent protection coverage across large tank surfaces, limited service life requiring frequent replacement, difficulty in monitoring system performance, and environmental compatibility concerns, prompting extensive research into advanced materials, innovative system designs, and intelligent monitoring technologies[5].

The emergence of controlled potential applications represents a paradigm shift toward more sophisticated and responsive corrosion protection strategiesio. Recent technological advances have opened new possibilities for enhancing CP system performance through the integration of smart monitoring capabilities, Internet of Things (IoT) technologies, and hybrid system configurations, with novel anode alloys offering improved electrochemical properties, extended service life, and enhanced environmental compatibility[6],[7]. Simultaneously, the development of predictive modeling tools and real-time monitoring systems is enabling more precise control over protection parameters and system optimization. The transition toward controlled potential applications reflects the industry’s recognition that passive protection systems may be insufficient for modern operational demands, offering dynamic adjustment of protection levels, improved coverage uniformity, and enhanced system reliability. This evolution represents a fundamental shift from traditional “set-and-forget” approaches toward active, responsive corrosion management strategies. Despite significant progress in materials science, system design, and monitoring technologies, substantial research gaps remain in the field, including predictive modeling capabilities for long-term performance optimization, incomplete standardization of controlled potential systems, and challenges in integrating advanced technologies with existing infrastructure, alongside economic considerations of transitioning to advanced CP systems. This comprehensive review aims to synthesize current knowledge regarding sacrificial anode cathodic protection systems for ASTs while identifying promising directions for future development, encompassing advances in anode materials, system design innovations, monitoring technology integration, and controlled potential applications [8].

By examining case studies, industrial applications, and technological developments, this work provides strategic insights for researchers, engineers, and industry practitioners working toward more effective and sustainable corrosion protection solutions, extending beyond technical considerations to address practical implementation challenges, economic factors, and environmental implications. By bridging the gap between fundamental research and industrial application, this work facilitates the adoption of next-generation corrosion protection technologies while maintaining operational reliability and cost-effectiveness .The findings contribute to the growing body of knowledge in electrochemical corrosion protection while highlighting opportunities for further research and development , supporting the evolution of AST corrosion protection from reactive maintenance approaches toward proactive, intelligent protection systems that ensure long-term structural integrity and operational safety while minimizing environmental impact and lifecycle costs [8].

- RELATED WORK

Aboveground storage tanks (ASTs) are vital infrastructure components in industries such as petroleum refining, chemical processing, water treatment, and power generation . These large structures, often containing hazardous or valuable materials, face constant threats from corrosion, particularly at the tank bottom due to soil moisture, groundwater, and contaminants, as well as external corrosion of tank shells and piping in aggressive environments[9].

The consequences of inadequate corrosion control can be severe, including structural failures, environmental contamination, regulatory penalties, and safety hazards. Consequently, regulatory agencies have enforced strict corrosion protection requirements, emphasizing the importance of advanced and reliable cathodic protection (CP) strategies within broader asset integrity management frameworks. Cathodic protection, one of the most widely used electrochemical corrosion control methods, operates by polarizing the structure to a potential where corrosion rates become negligible. Two main CP approaches exist: sacrificial anode cathodic protection (SACP) and impressed current cathodic protection (ICCP) [10].

SACP systems, which rely on galvanic coupling with metals such as zinc, magnesium, or aluminum alloys, are simple, self-regulating, and ideal for remote or hard-to-access installations. In contrast, ICCP systems, powered by external current sources, provide precise control and adaptability for complex geometries but require sophisticated monitoring, reliable power, and higher maintenance. While SACP is widely applied in AST protection due to its low cost, ease of installation, and reliable performance, challenges remain related to current output limitations, uniform protection, and service life. To address these limitations, recent research has explored both numerical modeling and practical optimization approaches. Complementary studies introduced hybrid approaches, such as electrochemical modeling in marine environments, simulations combined with empirical coating analysis, and further controlled-potential designs, highlighting both theoretical insights and practical advancements. Together, these studies underline the importance of integrating theoretical modeling with practical system-level innovations to achieve effective and sustainable corrosion protection in ASTs [11][12].

Table 1 Summarizing the Previous Studies

| Study | Methods Used | Results | Optimization Effectiveness |
| --- | --- | --- | --- |
| [1] | Numerical modeling using Direct Boundary Element Method (DBEM) + Newton-Raphson iterative solver for nonlinear boundary conditions | Accurate simulation of electric potential and current density over buried pipeline surfaces; valuable theoretical insight | Excellent for design and analysis, but lacks real-time control or direct system optimization |
| [2] | Potential-controlled design using zinc anodes in aboveground storage tanks | Improved protection uniformity; reduced anode wastage and excessive current | Effective, but less flexible than variable resistor system |
| [3] | Numerical simulation + experimental validation for coated/uncoated tank surfaces | Demonstrated that coating reduces anode consumption and extends protection lifespan | Helpful for efficiency but relies on passive mitigation rather than active control |
| [4] | Electrochemical modeling of SACP system in marine conditions | Highlighted the importance of anode material selection to avoid overprotection | Theoretical value only; no practical optimization or current regulation included |

## 3. Principles of Sacrificial Anode CP for ASTs

### 3.1 Electrochemical Mechanism

The fundamental operation of sacrificial anode cathodic protection relies on the electrochemical series and the principle of galvanic coupling. When a more active metal (lower in the electrochemical series) is electrically connected to a less active metal in an electrolytic environment, a galvanic cell is formed. The more active metal becomes the anode and undergoes oxidation (corrosion), while the less active metal becomes the cathode and is protected from corrosion. In AST applications, the sacrificial anode material must have a sufficiently negative potential relative to steel to drive protective current [13]. The electrochemical reactions occurring in a typical zinc anode system include the anodic reaction where zinc dissolves (Zn → Zn²⁺ + 2e⁻) and the cathodic reaction on the protected steel surface where oxygen reduction or hydrogen evolution occurs (O₂ + 4H⁺ + 4e⁻ → 2H₂O or 2H⁺ + 2e⁻ → H₂).

The driving voltage of the galvanic couple determines the available current for protection, while the resistance of the circuit (including anode resistance, electrolyte resistance, and structure resistance) controls the current magnitude. The protective current must be sufficient to shift the potential of the entire protected structure to a level where corrosion rates become acceptable, typically more negative than -850 mV versus copper-sulfate electrode (CSE) for steel in soil environments [14].

The current distribution from sacrificial anodes follows complex patterns influenced by electrolyte conductivity, structure geometry, and anode placement. For large ASTs, achieving uniform current distribution across the entire tank bottom requires careful consideration of anode spacing, size, and positioning. The current density must exceed the critical current density required for protection while avoiding excessive polarization that could lead to coating damage or hydrogen embrittlement[15] .

### 3.2 Common Anode Materials and Their Characteristics

Zinc alloys represent the most widely used sacrificial anode material for AST applications due to their favorable electrochemical properties and environmental compatibility. High-purity zinc anodes provide a driving voltage of approximately 250–300 mV relative to steel and offer excellent current efficiency with minimal passivation in most soil conditions. Zinc alloys are formulated with small additions of aluminum and cadmium to enhance mechanical properties and current output while maintaining good corrosion product solubility [16].

Magnesium alloys offer higher driving voltages (600–700 mV relative to steel) and are particularly effective in high-resistivity environments where maximum current output is required. However, magnesium anodes are more susceptible to passivation in certain soil conditions and may produce excessive current in low-resistivity environments, potentially leading to overprotection and coating damage. Standard magnesium alloys include AZ63, AZ31, and high-potential alloys designed for specific applications. Aluminum alloys have gained attention for specialized applications due to their high current capacity and excellent efficiency in marine and some soil environments. Aluminum-zinc-indium and aluminum-zinc-tin alloys provide intermediate driving voltages while offering superior current capacity per unit weight. However, aluminum anodes are susceptible to passivation in certain environments and require careful alloy design to maintain activation [17].

The selection of anode material depends on multiple factors including soil resistivity, environmental conditions, required current output, and service life expectations. Recent developments in anode metallurgy have focused on optimizing alloy compositions for specific applications, improving current efficiency, and enhancing environmental compatibility through reduced heavy metal content[18].

### 3.3 Typical System Design and Configuration for ASTs

AST cathodic protection systems typically employ distributed anode installations designed to provide uniform current distribution across the protected surfaces. For tank bottom protection, anodes are commonly installed in shallow trenches or impressed into the soil beneath and around the tank perimeter. The anode bed design must consider tank geometry, soil conditions, and current requirements while ensuring adequate separation between anodes to prevent mutual interference [19].

Anode spacing and sizing calculations are based on current requirement assessments derived from structure surface area, current density requirements, and environmental factors. Typical current densities for bare steel in soil range from 1–10 mA/m², with higher values required for aggressive conditions or when rapid polarization is needed. The total current requirement is distributed among the installed anodes based on their individual current output capabilities [20][21].

Cable connections between anodes and the protected structure must be designed for the service environment and expected current levels. Header cables typically connect multiple anodes to junction boxes, which then connect to the main structure through heavy-duty cables. All connections must be properly insulated and protected from corrosion to ensure system reliability throughout the design life. Monitoring and test facilities are integral components of modern CP systems, including permanent reference electrodes, test stations, and current measurement devices. These facilities enable regular system performance assessment and optimization throughout the service life, with recent designs incorporating remote monitoring capabilities and data logging systems for continuous performance tracking [22].

### 3.4 Performance Factors: Soil, Environment, Coatings, and Geometry

Soil characteristics significantly influence sacrificial anode performance and system design requirements. Soil resistivity directly affects current output and distribution, with high-resistivity soils limiting anode effectiveness and requiring closer spacing or larger anodes. Soil chemistry, including pH, chloride content, and sulfate levels, influences anode corrosion rates and current efficiency. Moisture content and seasonal variations affect system performance and must be considered in design calculations. Environmental factors beyond soil characteristics include groundwater conditions, stray current interference, and climatic effects [23]. Groundwater chemistry and flow patterns can significantly impact anode performance and longevity. Stray currents from nearby electrical systems or other CP installations can interfere with system operation and require mitigation measures. Temperature variations affect electrochemical reaction rates and must be considered in performance predictions. Coating systems interact with CP systems in complex ways that influence current requirements and distribution. High-quality coatings reduce current requirements by limiting the exposed metal surface area but may also affect current distribution uniformity. Coating defects create localized high-current-density areas that must be adequately protected[24] .

The interaction between CP and coatings requires careful consideration to avoid overprotection that could damage coating systems. Tank geometry and size present unique challenges for uniform current distribution. Large tank bottoms may experience uneven protection levels, with areas remote from anodes receiving insufficient current. Edge effects and geometric discontinuities can create preferential current paths that leave some areas underprotected. Advanced modeling techniques are increasingly used to optimize anode placement and predict current distribution patterns for complex geometries [25].

5. Comparative Analysis

The evolution of sacrificial anode cathodic protection (SACP) systems for aboveground storage tanks has reached a critical stage where traditional passive approaches are increasingly being challenged by controlled potential systems. Comparative assessments across performance dimensions highlight both the enduring value of conventional methods and the transformative potential of newer, adaptive solutions. Traditional sacrificial anode systems, based on simple galvanic action, have been widely used for decades due to their proven reliability, operational simplicity, minimal training requirements, and low capital costs . These characteristics make them particularly suitable for small to medium tank installations, stable environments, and budget-constrained projects [26]. However, their limitations are well documented. Current distribution tends to be uneven, especially in tanks larger than 30–40 meters, where central areas may be underprotected while perimeters are overprotected, resulting in potential variations of approximately ±200 mV. Additionally, their inability to adapt to environmental changes—such as variations in soil moisture, temperature, or salinity—leads to inconsistent performance [10, 20]. Oversizing to accommodate worst-case conditions often results in 20–30% excess current consumption, faster anode depletion, and increased lifecycle costs. Monitoring in these systems relies primarily on periodic surveys and visual inspections, providing only limited performance snapshots, while maintenance remains reactive and may require costly excavation, leading to premature anode replacement or unexpected failures [27].

Controlled potential systems address these challenges by incorporating advanced monitoring, intelligent control, and adaptive current distribution technologies. They provide uniform protection within ±50 mV across the tank surface, offering 15–25% better coverage than traditional systems[28]. Real-time monitoring enables dynamic adjustments to account for structural geometry, soil variations, and environmental fluctuations, ensuring consistent performance even under challenging conditions. By optimizing current efficiency and minimizing overprotection, these systems extend anode life by approximately 35% and reduce unnecessary material consumption, while preventing coating damage caused by over-polarization. Their adaptability makes them especially valuable in environments subject to seasonal or long-term variations. Although installation is more complex and initial capital costs are 40–60% higher due to the inclusion of sensors, electronics, and communication components, these expenses are offset by enhanced commissioning flexibility, remote monitoring, and optimization capabilities that allow continuous fine-tuning during operation.

In terms of monitoring and maintenance, controlled potential systems provide continuous data collection, trend analysis, and predictive maintenance[29]. This capability reduces downtime, decreases inspection frequency, and enables proactive interventions before failures occur. Advanced diagnostics allow for precise identification of system issues, facilitating targeted corrective actions, while remote connectivity enhances both safety and operational efficiency. From an economic perspective, although traditional systems appear less expensive initially, their higher current consumption, reactive maintenance needs, and limited adaptability significantly increase total lifecycle costs. In contrast, controlled potential systems lower the total cost of ownership by extending anode life, minimizing emergency repairs, and optimizing maintenance schedules, often achieving payback within 5–7 years for large-scale installations [30].

Risk and reliability assessments further underscore these trade-offs. Traditional systems are inherently simple, with few failure modes; however, their lack of diagnostic visibility and adaptability leaves them vulnerable to hidden degradation and unexpected failures. Controlled potential systems, though more complex due to their electronic components, provide redundancy, early fault detection, and continuous performance monitoring, thereby achieving superior reliability. Environmental and safety factors also differentiate the two approaches. Traditional systems may pose disposal challenges, particularly when older alloys contain environmentally harmful elements, whereas controlled potential systems reduce environmental impact by minimizing material consumption and enabling data-driven oversight of safety and regulatory compliance. Nevertheless, they require careful management of electronic and electrical components to maintain system integrity [31].

Performance metrics consistently demonstrate the superiority of controlled potential systems, offering up to four times better protection uniformity, 20–30% higher current efficiency, real-time monitoring instead of periodic inspections, extended anode life, and predictive rather than reactive maintenance strategies. Qualitatively, traditional systems excel in simplicity, affordability, and long-standing reliability but remain constrained by their passive operation. In contrast, controlled potential systems deliver adaptability, optimization, and comprehensive monitoring—enhancing performance and sustainability—at the cost of higher complexity and the need for specialized technical expertise [32].

Application suitability ultimately depends on contextual factors and operational requirements. Traditional sacrificial anode systems remain suitable for small tanks, stable environments, remote locations, and budget-limited projects where simplicity, low maintenance, and cost-effectiveness are key considerations. In contrast, controlled potential systems deliver maximum value in large-scale or critical installations, aggressive or variable environments, and facilities that require integration with advanced asset management and monitoring systems. While incremental advances in anode materials, coatings, and configuration design may continue to improve the performance and durability of traditional systems, their inherently passive nature limits the potential for transformative improvements. Controlled potential systems, on the other hand, provide a dynamic platform for continuous technological evolution. Innovations in sensor technology, AI-driven control algorithms, IoT-based communication, and digital infrastructure are expected to further enhance optimization, adaptability, and system intelligence, positioning these systems as the cornerstone of next-generation corrosion protection strategies[33] [34].

Table 2 Key Differences between Traditional SACP and Controlled Potential System

| Criteria | Traditional SACP (Sacrificial Anode) | Controlled Potential CP |
| --- | --- | --- |
| Installation & Cost | Low initial cost, simple design, minimal power requirements | Higher initial investment, requires power source and advanced design |
| Operation | Passive, self-regulated by anode potential | Active control with adjustable output and feedback mechanisms |
| Protection Uniformity | Uneven distribution in large tanks, risk of under/over-protection | Uniform protection across structures with precise potential control |
| Maintenance | Periodic checks, mostly reactive | Real-time monitoring, predictive maintenance, IoT integration |
| Anode Life | Shorter due to continuous consumption | Longer lifespan due to optimized current distribution |
| Environmental Impact | Higher metal waste, possible overprotection side effects | Reduced waste, better environmental compatibility |
| Suitability | Small to medium tanks, remote sites, budget-limited projects | Large, critical, or high-risk installations where reliability is crucial |

Figure 1 Table   Bar Chart Data Idea (Performance Comparison)

Figure 1 illustrates a bar chart comparing the performance of the Traditional Sacrificial Anode Cathodic Protection (SACP) system and the Controlled Potential Cathodic Protection (CP) system across several key performance metrics [35]. On the X-axis, the chart presents the evaluated performance parameters, including Protection Uniformity, Current Efficiency, Maintenance Ease, Anode Life, Environmental Compatibility, Installation Complexity, and Monitoring Capability, while the Y-axis ranges from 0 to 100, representing the relative performance level for each metric. Each parameter is represented by two adjacent bars: the blue bar corresponds to the Traditional SACP system, whereas the green bar represents the Controlled Potential CP system. The comparison clearly indicates that the Controlled Potential CP system outperforms the traditional approach in most performance aspects—particularly in protection uniformity, current efficiency, anode life, environmental compatibility, and monitoring capability—while the traditional system maintains relative advantages in maintenance ease and lower installation complexity. This visual representation provides an intuitive and effective means of comparing both systems, highlighting their respective strengths and trade-offs in a concise and accessible manner.

# 6. Challenges and Future Directions

# Sacrificial anode cathodic protection systems for aboveground storage tanks face multifaceted challenges that require comprehensive technological and methodological solutions. The most pressing challenge remains achieving consistent protection across large tank structures, particularly in installations exceeding 30–40 meters in diameter, where current attenuation effects create significant protection variations[36]. Traditional systems often experience current density fluctuations of ±200 mV across tank surfaces, leaving central areas underprotected while perimeters receive excessive current, potentially damaging protective coatings. Environmental compatibility issues compound these problems, as conventional anode materials containing cadmium and mercury create soil contamination concerns[37], while soil chemistry variations and seasonal moisture changes dramatically affect system performance predictability. Service life limitations further challenge system reliability, with rapid anode consumption in aggressive environments requiring frequent maintenance interventions that increase operational costs and system downtime. Moreover, stray current interference from nearby electrical installations and AC power systems accelerates anode degradation while creating unpredictable performance patterns that traditional DC measurements fail to detect adequately[38].

# Future directions in sacrificial anode technology center on controlled potential applications that integrate smart monitoring systems with adaptive current regulation capabilities.[39] These advanced systems promise to overcome current limitations through real-time potential monitoring, intelligent control algorithms, and IoT-based communication networks that enable continuous performance optimization [40][41]. Research priorities include developing novel anode materials incorporating nanostructured surfaces, biodegradable compositions, and smart materials that respond automatically to environmental conditions. Artificial intelligence and machine learning applications show significant promise for predictive maintenance strategies, with advanced algorithms analyzing performance patterns to optimize current distribution and predict system degradation before failures occur. Additionally, digital twin technologies are emerging as transformative tools for system design and optimization, combining real-time monitoring data with sophisticated multi-physics simulations to create virtual representations of physical installations that enable advanced analysis and predictive maintenance capabilities [42][43].

## The transition toward hybrid systems combining sacrificial and impressed current technologies represents another critical development pathway, offering the reliability of passive systems with the precision and adaptability of active control. Advances in material science are focusing on environmentally sustainable anode compositions that utilize recycled materials and bio-derived components while maintaining superior electrochemical performance characteristics [44]. Standardization efforts are increasingly necessary to address regulatory requirements for advanced cathodic protection (CP) systems, particularly controlled potential applications that current standards inadequately cover. Furthermore, integrating CP systems with comprehensive asset integrity management platforms requires the development of standardized communication protocols and data-sharing frameworks that facilitate coordinated infrastructure protection strategies. Long-term monitoring capabilities, supported by advanced sensor technologies and energy harvesting systems, will enable continuous performance assessment over extended periods without reliance on external power sources. Addressing these emerging challenges through collaborative research involving academia, industry, and regulatory bodies will be essential to determine whether next-generation cathodic protection systems can achieve the desired levels of enhanced performance, environmental sustainability, and cost-effectiveness necessary to safeguard critical infrastructure in increasingly demanding operational environments [45].

## Table 3 Current Challenges in Sacrificial Anode CP Systems for ASTs

| Challenge Category | Specific Challenge | Study/Source | Impact Level | Description |
| --- | --- | --- | --- | --- |
| Protection Uniformity | Inconsistent current distribution in large tanks | Review Analysis, 2024 | High | Current density variations of ±200mV across tank surfaces, central areas are underprotected |
| Protection Uniformity | Edge effects and geometric discontinuities | Multiple Case Studies | High | Tank peripheries receive higher current while central areas experience deficiency[ |
| Protection Uniformity | Current attenuation in tanks >30-40m diameter | Industrial Applications | High | Remote areas from anodes receive insufficient current density for adequate protection |
| Service Life Limitations | Rapid anode consumption rates | Jawad et al., 2020 | High | Traditional systems consume anodes 35x faster than optimized controlled systems |
| Service Life Limitations | Environmental acceleration of degradation | Environmental Studies | Medium | Aggressive soil conditions and stray currents accelerate consumption beyond predictions |
| Service Life Limitations | Maintenance access difficulties | Field Experience Reports | Medium | Underground installations require extensive excavation for replacement |
| Environmental Compatibility | Heavy metal contamination (Cd, Hg) | Environmental Compliance Research | High | Traditional anode alloys create soil contamination requiring remediation |
| Environmental Compatibility | Soil chemistry interactions | Multiple Studies | Medium | Acidic soils accelerate consumption while alkaline conditions cause passivation |
| Environmental Compatibility | Stray current interference | AC Interference Studies | Medium | Industrial electrical systems cause erratic performance and accelerated degradation |
| Potential Control | Overprotection in low-resistivity environments | Mujezinović & Martinez, 2022 | Medium | Excessive current causes coating damage and hydrogen embrittlement risks |
| Potential Control | Underprotection in high-resistivity soils | Design Optimization Studies | High | Insufficient current output fails to achieve adequate protection potentials |
| Potential Control | Inability to adapt to changing conditions | System Performance Analysis | High | Self-regulating nature limits response to environmental or operational changes |
| Monitoring Limitations | Reactive maintenance approaches | Digital Integration Studies | Medium | Periodic surveys provide only snapshots, missing gradual performance changes |
| Monitoring Limitations | Limited diagnostic capabilities | Field Application Reports | Medium | Traditional DC measurements fail to detect AC interference and complex issues |
| Economic Factors | High lifecycle costs from frequent replacement | Economic Analysis Studies | High | Initial cost advantages offset by maintenance requirements and system downtime |
| Economic Factors | Oversizing for worst-case conditions | Design Practice Review | Medium | Systems designed for extreme conditions waste 20-30% excess current in normal operation |

## Table 4 Future Directions and Research Priorities

| Future Direction Category | Specific Development | Research Status | Timeline | Expected Impact |
| --- | --- | --- | --- | --- |
| Controlled Potential Systems | Real-time potential monitoring with feedback control | Active Research | 2-5 years | Eliminate over/underprotection issues, achieve ±50mV uniformity |
| Controlled Potential Systems | IoT-integrated smart monitoring networks | Pilot Projects | 1-3 years | Enable continuous remote monitoring and predictive maintenance |
| Controlled Potential Systems | Artificial intelligence optimization algorithms | Development Phase | 3-7 years | Automated system optimization and performance prediction |
| Advanced Materials | Nanostructured anode compositions | Laboratory Research | 5-10 years | Enhanced current density and controlled dissolution rates |
| Advanced Materials | Biodegradable and eco-friendly anodes | Early Research | 7-15 years | Complete environmental compatibility with maintained performance |
| Advanced Materials | Smart materials with environmental responsiveness | Conceptual Stage | 10+ years | Self-regulating systems that adjust to conditions automatically |
| Hybrid Systems | Sacrificial-impressed current combinations | Field Testing | 2-5 years | Combine the reliability of passive systems with precision of active control |
| Hybrid Systems | Switchable protection modes | Development Phase | 3-5 years | Enable system adaptation to changing operational requirements |
| Hybrid Systems | Zone-specific protection strategies | Design Phase | 2-4 years | Optimize protection methods for different areas of same structure[10, 20] |
| Digital Technologies | Digital twin implementations | Pilot Projects | 3-7 years | Virtual system optimization and predictive analysis capabilities |
| Digital Technologies | Machine learning for predictive maintenance | Active Development | 2-5 years | Predict failures before occurrence and optimize maintenance schedules |
| Digital Technologies | Blockchain for asset integrity tracking | Conceptual Stage | 5-10 years | Immutable records of protection system performance and maintenance |
| Modeling and Simulation | Multi-physics simulation platforms | Development Phase | 3-7 years | Accurate prediction of complex electrochemical-environmental interactions |
| Modeling and Simulation | Uncertainty quantification methods | Research Phase | 5-10 years | Probabilistic design approaches accounting for environmental variability |
| Modeling and Simulation | Real-time model updating systems | Early Development | 5-8 years | Dynamic models that improve accuracy based on monitoring data |
| Standardization | Controlled potential system standards | Development Phase | 3-5 years | Industry-wide adoption guidelines and performance benchmarks |
| Standardization | Environmental compliance protocols | Active Development | 2-4 years | Clear guidelines for sustainable anode material selection and disposal |
| Standardization | Integration with asset integrity management | Planning Phase | 3-7 years | Coordinated approach to infrastructure protection and monitoring |
| Sustainability | Circular economy approaches for anode materials | Research Phase | 7-15 years | Recycling and reuse strategies for consumed anode materials |
| Sustainability | Life cycle assessment integration | Active Research | 2-5 years | Comprehensive environmental impact evaluation throughout system lifecycle |
| Sustainability | Zero-waste CP system designs | Conceptual Stage | 10+ years | Complete elimination of waste products from cathodic protection systems |

## 10. Conclusion

This review highlights the current state and future prospects of sacrificial anode cathodic protection systems for aboveground storage tanks, with emphasis on the shift toward controlled potential applications. Advances in anode materials, system design, and smart monitoring technologies, including IoT-based solutions, have improved performance, environmental compatibility, and predictive maintenance. However, challenges remain in ensuring uniform protection, managing lifecycle costs, and meeting environmental requirements. Controlled potential systems present a paradigm shift, combining the reliability of sacrificial systems with the precision of impressed current systems, offering improved efficiency and reduced costs but requiring specialized expertise and higher initial investment. Case studies show both benefits and challenges, emphasizing the need for proper design, site assessment, and monitoring. Future progress will likely focus on innovative materials, advanced modeling, sustainability, and digital integration. Research gaps include predictive modeling, standardization, sustainable anodes, and integration with asset integrity management. Addressing these requires collaboration among researchers, industry, and regulators. Ultimately, the evolution toward controlled potential systems is both a technological opportunity and a strategic necessity for ensuring infrastructure integrity, demanding ongoing innovation, standardization, and commitment from all stakeholders.

Disclaimer (Artificial intelligence)

Author(s) hereby declare that NO generative AI technologies such as Large Language Models (ChatGPT, COPILOT, etc.) and text-to-image generators have been used during the writing or editing of this manuscript.

## References

[1]	K. Amaya and S. Aoki, “Optimum design of cathodic protection using,” vol. 48, pp. 25–36.

[2]	W. D. Program, “Developing a Procedure to Determine Applicability of Vapor Corrosion Inhibitors for Soil Side Protection of Aboveground Storage Tanks,” 2025.

[3]	A. Stoicescu, R. G. Ripeanu, T. Maria, C. Nicolae, and L. Toader, “Multifactorial Analysis of Defects in Oil Storage Tanks : Implications for Structural Performance and Safety,” pp. 1–35, 2025.

[4]	S. C. Sulfate-magnesium, “Standard Test Method for Laboratory Evaluation of Magnesium Sacrificial Anode Test Specimens for Underground Applications 1,” vol. 11, no. Reapproved, pp. 3–6, 2002.

[5]	A. Advanced, A. Scientific, and B. Almassri, “CATHODIC PROTECTION OF CORRODED REINFORCED CONCRETE STRUCTURE ةينورتكللإا تاع زانملا هميسوك ينورتكللإا ميكحتلا ةمكآتملا ةحمدملا ةيناسرخلا لكايهمل ةيدوثاكلا ةيامحلا Abstract : increased significantly since 1975 . Corrosion poses a significant challenge in maintaining infrastructure , as it causes,” no. 19, pp. 1–18, 2025.

[6]	H. H. Qasim, A. E. Hamza, L. Audah, H. H. Ibrahim, H. A. Saeed, and M. I. Hamzah, “Design and implementation home security system and monitoring by using wireless sensor networks WSN/internet of things IoT,” Int. J. Electr. Comput. Eng., vol. 10, no. 3, pp. 2617–2624, Aug. 2020, doi: 10.11591/ijece.v10i3.pp2617-2624.

[7]	H. H. Qasim, A. M. Jasim, and K. A. Hashim, “Real-time monitoring system based on integration of internet of things and global system of mobile using Raspberry Pi,” vol. 12, no. 3, pp. 1418–1426, 2023, doi: 10.11591/eei.v12i3.4699.

[8]	M. F. Pereira, M. Teresa, G. Barbosa, and L. De, “The Sustainability Profile of New Technologies for the Repair of Corroded Reinforced Concrete Structures The Sustainability Profile of New Technologies for the Repair of Corroded Reinforced Concrete Structures”, doi: 10.1088/1755-1315/1536/1/012040.

[9]	S. Anwar, Y. Octavitri, I. Purnaningratri, and I. M. Sofian, “Electrochemical Performance of Sacrificial Anode Metals in Preventing Corrosion on Ships : A Literature Review,” vol. 4, no. 1, pp. 2208–2216, 2025.

[10]	A. Alamiery and L. M. Shaker, “Smart and green corrosion inhibitors : Mechanisms , computational tools , and sustainable protection strategies,” vol. 348, no. September 2025, 2026.

[11]	F. Budiman et al., “Integrating IoT-enabled automated impressed current cathodic protection systems with metal potential monitoring : a digital technology approach to address corrosion for promoting environmental ecosystem conservation,” Measurement, vol. 258, no. PB, p. 119167, 2026, doi: 10.1016/j.measurement.2025.119167.

[12]	A. Jospine, L. Hanif, M. Audah, A. Hamzah, and H. Qasim, “Journal of Electronics Voltage and Application Vehicle Monitoring System with Geofencing Capability,” J. Electron. Volt. Appl., vol. 1, no. 2, pp. 1–13, 2020, doi: 10.30880/jeva.2020.01.02.001.

[13]	S. Abiola, A. Patricia, I. Popoola, and D. Toyin, “Evaluation of the electrical properties of carbon electrodes developed with bio-material additions as a sacrificial anode in cathodic protection,” Next Mater., vol. 1, no. 4, p. 100050, 2023, doi: 10.1016/j.nxmate.2023.100050.

[14]	F. Augusto, N. Perez, U. Politécnica, D. L. Cárdenas, and C. P. Michoacán, “Electrochemical modulation of annealed steel via cupric sulfate , potassium chloride and trisodium citrate : insights into redox behaviour and corrosion resistance,” vol. 15, no. 3, pp. 1–21, 2025.

[15]	M. R. Akram, “Identification of Factors Influencing Sustainability of Buried Continuous Pipelines,” 2020.

[16]	R. Wang et al., “Numerical simulation design and optimization of regional cathodic protection in a large oil and gas station,” no. December, pp. 1–12, 2025, doi: 10.3389/fceng.2025.1679306.

[17]	D. H. Kroon and M. Urbas, “Cathodic Protection of Above Ground Storage Tank Bottoms by”.

[18]	D. Yang et al., “Engineering 3D copper foam current collectors : modification strategies and challenges toward stable lithium metal batteries,” Sci. Technol. Adv. Mater., vol. 26, no. 1, 2025, doi: 10.1080/14686996.2025.2525064.

[19]	G. Kear, “Electrochemical corrosion of unalloyed copper in chloride media –– a critical review,” vol. 46, pp. 109–135, 2004, doi: 10.1016/S0010-938X(02)00257-3.

[20]	X. Xie, “Design of New Al Photoanode Composite for Cathodic Protection Based on Photocatalytic Material and Sacrificial Anode Design of New Al Photoanode Composite for Cathodic Protection Based on Photocatalytic Material and Sacrificial Anode”, doi: 10.1149/2.0321905jes.

[21]	A. E. Hamza et al., “Design and implement WSN/IOT smart parking management system using microcontroller,” Int. J. Electr. Comput. Eng., vol. 10, no. 3, pp. 3108–3115, 2020.

[22]	M. A. Caronge, “COMBINATION OF IMPRESSED CURRENT AND SACRIFICIAL ANODE CATHODIC PREVENTION TO IMPROVE CORROSION PREVENTION SYSTEM IN REINFORCED CONCRETE COMBINATION OF IMPRESSED CURRENT AND SACRIFICIAL ANODE CATHODIC PREVENTION TO IMPROVE CORROSION PREVENTION SYSTEM IN,” 2020.

[23]	H. M. H. Farh, M. El, A. Ben, and T. Zayed, “A comprehensive review of corrosion protection and control techniques for metallic pipelines,” Eng. Fail. Anal., vol. 143, no. PA, p. 106885, 2023, doi: 10.1016/j.engfailanal.2022.106885.

[24]	E. M. Shaalan, M. A. Mostafa, A. Salam, and M. Al-gabalawy, “Cathodic Protection Performance Improvement of Metallic Pipelines based on Different DC Compensation Methods,” vol. 210, no. May, 2022.

[25]	S. Lin, J. Zhang, X. Liu, X. Zhang, Z. Cai, and X. Chen, “Study on Distribution Characteristics of Metro Stray Current and Evaluation of Cumulative Corrosion Effect,” vol. 2022, 2022, doi: 10.1155/2022/6845847.

[26]	N. Krishnan, D. K. Kamde, Z. Doosa, R. G. Pillai, D. Shah, and R. Velayudham, “Long-term performance and life-cycle-cost benefits of cathodic protection of concrete structures using galvanic anodes,” J. Build. Eng., vol. 42, no. March, p. 102467, 2021, doi: 10.1016/j.jobe.2021.102467.

[27]	S. Ahmed, V. Orth, M. Foley, K. Kottas, and C. Teodoriu, “Journal of Natural Gas Science and Engineering Designing in-house cathodic protection system to assess the long-term integrity of natural gas pipelines,” J. Nat. Gas Sci. Eng., vol. 94, no. May, p. 104116, 2021, doi: 10.1016/j.jngse.2021.104116.

[28]	I. Toor, “International Journal of Electrochemical Science Artificial intelligence and machine learning in corrosion inhibitor design & development : Advances , challenges , and future perspectives,” Int. J. Electrochem. Sci., vol. 21, no. 2, p. 101274, 2026, doi: 10.1016/j.ijoes.2025.101274.

[29]	L. B. Coelho, “Reviewing machine learning of corrosion prediction in a data-oriented perspective,” 2022, doi: 10.1038/s41529-022-00218-4.

[30]	S. Martinez, “SACRIFICIAL ANODE CATHODIC PROTECTION SYSTEM MODELLING USING DIRECT BOUNDARY,” vol. 16, pp. 25–30, 2022, doi: 10.2478/bhee-2022-0010.

[31]	R. Aalund and V. P. Paglioni, “Enhancing Reliability in Embedded Systems Hardware : A Literature Survey,” IEEE Access, vol. 13, no. January, pp. 17285–17302, 2025, doi: 10.1109/ACCESS.2025.3534138.

[32]	E. Entezari, A. Kumar, H. Mousavi, J. Luis, and G. Velazquez, “Materials Characterization A cost-effective model for synergistic effects of microstructure and crystallographic texture on hydrogen-induced crack growth and corrosion rates in pipeline steels,” Mater. Charact., vol. 223, no. February, p. 114917, 2025, doi: 10.1016/j.matchar.2025.114917.

[33]	A. Chehri, H. Chehri, N. Hakim, and R. Saadane, “Realistic 5.9 GHz DSRC Vehicle-to-Vehicle Wireless Communication Protocols for Cooperative Collision Warning in Underground Mining,” Smart Innov. Syst. Technol., vol. 185, no. June, pp. 133–141, 2020, doi: 10.1007/978-981-15-5270-0_12.

[34]	A. M. Jasim, H. H. Qasim, E. H. Jasem, and R. H. Saihood, “An internet of things based smart waste system,” Int. J. Electr. Comput. Eng., vol. 11, no. 3, pp. 2577–2585, Jun. 2021, doi: 10.11591/ijece.v11i3.pp2577-2585.

[35]	L. Zhu, X. Zhang, D. Li, J. Li, Z. Wang, and R. Tian, “An experimental and numerical study on the corrosion characteristics of weathering steel-concrete composite beams,” Constr. Build. Mater., vol. 462, no. October 2024, p. 139893, 2025, doi: 10.1016/j.conbuildmat.2025.139893.

[36]	N. Ganesh, R. S. M. Asce, and N. C. Moharana, “ADVANCED METHODS OF CORROSION MONITORING- A REVIEW,” pp. 413–420, 2015.

[37]	S. Hanif, S. Ali, A. H. Chaudhry, N. Sial, A. Marium, and T. Mehmood, “A Review on Soil Metal Contamination and its Environmental Implications,” 2025.

[38]	C. Wen, H. Tsai, S. Hsu, and H. Yeh, “Environmental Impact Assessment of Sacrificial Anode Method in Taiwan Strait,” pp. 622–635, 2020, doi: 10.4236/jep.2020.118037.

[39]	H. H. Qasim, H. Z. Abidin, S. Afzal, and C. Abdullah, “Handover management in vehicle communication : applications , techniques , issues , and challenges : a review,” vol. 13, no. 5, pp. 3167–3186, 2024, doi: 10.11591/eei.v13i5.7549.

[40]	M. A. Al-Shareeda, A. A. Alsadhan, H. H. Qasim, and S. Manickam, “Software defined networking for internet of things: review, techniques, challenges, and future directions,” Bull. Electr. Eng. Informatics, vol. 13, no. 1, pp. 638–647, 2024, doi: 10.11591/eei.v13i1.6386.

[41]	M. Ridha, S. Huzni, S. Fonna, A. K. Ariffin, and A. R. Daud, “Optimization of Cathodic Protection System Design for Pipe-Lines Structure with Ribbon Sacrificial Anode Using BEM and GA,” pp. 3–8.

[42]	N. Abbood and I. Al, “Cathodic Protection for Above Ground Storage Tank Bottom Using Data Acquisition,” vol. 21, no. 7, 2015.

[43]	M. A. Al-Shareeda, A. A. Alsadhan, H. H. Qasim, and S. Manickam, “Long range technology for internet of things: review, challenges, and future directions,” Bull. Electr. Eng. Informatics, vol. 12, no. 6, pp. 3758–3767, 2023, doi: 10.11591/eei.v12i6.5214.

[44]	P. Taylor, M. Shehadeh, and I. Hassan, “Ships and Offshore Structures Study of sacrificial cathodic protection on marine structures in sea and fresh water in relation to flow conditions,” no. September 2013, pp. 37–41, doi: 10.1080/17445302.2011.590694.

[45]	D. Of, A. C. Protection, A. Corrosion, F. Marine, and M. E. Programme, “Certification of approval,” no. January, 2008.