Towards Durable Solar Energy System: A Review of Corrosion Challenges and Emerging Protection Technologies

Abstract

An important element influencing the longevity and efficiency of solar panels is corrosion, which is examined in this review paper along with its mechanism, detection techniques, and mitigation options. Encapsulants, backsheets, and metallic components interact intricately to cause corrosion, which is a result of material deterioration and exposure to the environment. Though they have limits in terms of cost and field usability, advanced detection techniques such as acoustic emission monitoring, electrochemical impedance spectroscopy, and infrared thermography offer insights into early-stage corrosion. Preventive measures that increase the robustness of solar panels include self-healing coatings, corrosion-resistant polymers, and UV-resistant encapsulants. Furthermore, accelerated aging tests and environmental monitoring systems aid in the comprehension of corrosion behavior under diverse circumstances. Nonetheless, obstacles including exorbitant implementation expenses, restricted scalability, and incompatibilities with current systems underscore the necessity of comprehensive strategies. This review comparatively examines corrosion mechanisms affecting key photovoltaic components alongside existing detection, prevention, and mitigation strategies, highlighting their relative effectiveness, limitations, and suitability across different environmental conditions to inform more durable and standardized PV system designs.

Keywords: Solar panels, corrosion, photovoltaic degradation, corrosion detection, mitigation strategies, renewable energy.

Introduction

One of the most common issues in the field of solar module is corrosion, which results in ribbon discoloration [1] [2]. Since corrosion mechanisms might be linked to other types of degradation, determining the origin of a PV module's corrosion may not be simple [3] [4]. Any component of the PV module that deteriorates can lead to corrosion as show in figure 1, which allows oxygen and water to enter the solar cell [5] [6]. An electrolyte, an oxidizing agent, and a metal are necessary for corrosion to happen in a PV module [2]. According to a recent study, the most significant contributing causes to corrosion are the degradation of the encapsulant and backsheet [7].When the PV module is exposed to outside UV radiation, heat, and relative humidity, ethylene vinyl acetate (EVA) degrades. The laminated EVA produces acetic acid in the event of a malfunctioning module, hastening the corrosion of metal. There is a reciprocal cause-and-effect link between the various conditions that originate and exacerbate corrosion in solar modules [3]. An overview of the corrosion mechanisms in PV modules described in earlier research is provided in Fig. 5. Regarding the corrosion effect, which arises from the degradation of the EVA encapsulant, they are in accord [8] [9] [10]. Figure 2 shows EVA delamination issues brought on by inadequate lamination parameters and environmental factors have been the subject of several research [8] [11] [12]. Others have employed pyrolysis and hydrolysis following exposure to moisture and high temperatures to focus on the production of acetic acid [13] [14].The corrosion phases and interactions between the galvanic pairs are depicted in Fig 6. PV module corrosion causes power loss and a progressive rise in series resistance [15] [16]. The oxidation potentials of Ag/Ag(I), Sn/Sn(II), Cu/Cu(II), Al/Al(III), and Pb/Pb(II) were, 0.799 V, -0.136, 0.337, -1.662, and -0.358 respectively [2] [17].  Because metals with lower oxidation potentials serve as sacrificial anodes in galvanic couples [18], they experience higher rates of corrosion [19]. When water comes into contact with the solder joints on the front side of the solar cell, corrosion starts to happen. The series resistance will then rise as the corrosion gradually moves toward the center, decreasing the Ag-solder contact [17]. The solder junction and aluminum contact corrode first on the back side [20] [21]. Other metals will start to corrode as the corrosion worsens and the metal is consumed.

Selection of corrosion-resistant structural materials, such as specialized aluminum alloys or stainless steel for frames and connectors, is foundational to extending module lifetime. These materials demonstrate lower corrosion rates in saline and high-humidity environments compared to conventional metals, improving reliability and reducing maintenance costs.[183]

-

Fig.  1. Silicon solar cells' corrosion mechanism [5] [2] [4]. Hydrogen gas is created during corrosion when H2O and O2 enter via the backsheet or frame edges and pass through a delaminated encapsulant-cell gap. Delamination is accelerated by the growth and merging of the gas bubbles

Fig.  2 Corrosion steps for the front and rare side of solar cell [11].

Protective Coatings

Recent research shows that advanced coatings, especially heterostructure and hybrid coatings, can reduce corrosion currents dramatically. For instance, TiO₂/C₃N₄ heterostructure coatings on aluminum frames achieved ~78% reduction in corrosion current density under simulated conditions. [184]

| Coating Type | Mechanism | Performance Notes |
| --- | --- | --- |
| TiO₂/C₃N₄ heterostructure | Photocathodic protection + barrier | 78% corrosion reduction in aluminum frames under light exposure. |
| Nano-container self-healing coatings | Controlled release of inhibitors | Responsive inhibitor release, improved long-term defense. |
| Hybrid sol–gel coatings | Passive barrier + corrosion prevention | Broad applicability; effective in atmospheric environments |

Table 1: Protective coatings span a range of functional mechanisms, from passive barriers to active corrosion-inhibitor delivery. Photocathodic coatings such as TiO₂/C₃N₄ heterostructures not only serve as barriers but also facilitate charge separation that suppresses corrosion currents, showing significant reduction rates in accelerated tests. Nanocontainer-based and hybrid sol–gel coatings introduce controlled inhibitor release and multifunctional barrier properties suitable for diverse PV deployment conditions. [184]

Corrosion Detection Mechanism in Solar Cell

Visual Inspection

One of the fundamental techniques used for corrosion detection [22] and other modes of degradation in solar panels is visual inspection as seen in Figure 3 below [23]. It helps facilitate early detection and mitigation of probable performance losses [24]. According to a study by Daher et al., visual examinations showed that 50% of the modules had encapsulant discoloration, and 30% had frame corrosion [25]. These findings underscored how susceptible solar panels are to external stresses over time. Similar to this, a study by D. H. Daher et al., examined 48 photovoltaic (PV) modules and found that bubbling and snail trails were common problems, occurring in 93.7% of the units examined [26]. This suggests the importance of routine visual inspection in spotting minor significant flaws in PV. Furthermore, an article published by Aboagye et al.'s showed how visual inspection methods was used in Ghana to detect discoloration and fracture formation which was manifested as a result of high humidity and temperature accelerating deterioration [27]. According to Al Mahdi et al.'s (2024), visual inspection identified corrosion in 35% of an analysis of photovoltaic systems [28]. This finding was profoundly associated with the local environmental conditions, suggesting that visual assessment is essential for maintenance [29]. In total consideration, these studies illustrated how visual inspection methods can be helpful early detection of corrosion and degradation in solar panels, providing imperative novel evidence about how environmental influences might affect the durability and effectiveness of modules.

Fig.  3.  Image shows visual inspection of a corroded solar panel [14].

Infrared (IR) Thermography

One of the fundamental non-destructive diagnostic techniques used in identifying solar panel corrosion is Infrared Thermography  [22] [23]. As Depicted in figure 4, Infrared Thermography is key in enabling for spotting corrosion earlier to ensure preventive maintenance and longevity of a photovoltaic system [24]. Infrared Thermography detect corrosion and microcracks by detecting thermal irregularities from measuring the infrared radiation that a solar module releases [25] [26] [27].  S. Gallardo-Saavedra work demonstrated how Infrared thermography is useful in identifying problem hotspots, and when done early facilitate prompt maintenance and increase efficiency [28]. Other finding as in the case of L. H. Callejo et al., thermal imaging was also used to illustrate how temperature variations are highly correlated with corrosion damages [29].Further studies, such as those conducted by Ballestín-Fuertes et al., highlight the importance of using Infrared thermography as a non-invasive examinations for deformation detection on solar farms and informing maintenance planning [30]. To improve detection and control of corrosion in photovoltaic systems, J. I. Morales-Aragonés et al. to a step further by combining thermography with sophisticated analytical methods, his approach was also key in providing accurate data [31]. These observations taken together highlight the critical role that infrared thermography plays in the sustainable management of solar energy installations, guaranteeing efficient operation and extended lifespans.

Fig.  4. IR thermogram of a broken (cracked) solar panel [16].

Electrochemical Impedance Spectroscopy (EIS)

Electrochemical Impedance Spectroscopy (EIS) offers real-time monitoring [32] [33] and detailed analysis of the corrosion processes  [34] [35]. For instance, EIS was used to assess the corrosion properties of several materials in contact with molten salts in the work by Encinas-Sánchez et al. (2023), this was useful in identifying the pathway of deterioration in the solar energy applications [36]. In a similar vein, Wang et al., used EIS to examine the corrosion behavior of metallic material in a molten carbonate environment, providing important new information on how corrosion starts and outlining a course for improving safeguards in solar power systems [37]. Finally, in a study by González et al., Electrochemical Impedance Spectroscopy (EIS) was used on steel subjected to molten salt, it was able to successfully distinguish between distinct corrosion pathways, providing a useful information for creating materials with improved corrosion resistance in CSPs [38]. From these experiments, Electrochemical Impedance Spectroscopy is seen to have shown significant contribution to corrosion detection technique, allowing for better material selection and maintenance plans.

Acoustic Emission (AE) Monitoring

Acoustic Emission Monitoring has proven to be a useful method for identifying corrosion in solar panels, offering real-time information on structural integrity [40] [41] [42]. In order to facilitate early identification and preventive maintenance, current research has shown that acoustic emission as in  figure 5 can be used to distinguish between different phases of corrosion. A substantial correlation was seen between acoustic emission signals and corrosion progression in an experimental assessment conducted by Anastasopoulos et al., this is usefully in prompting early treatments [43]. Furthermore, Geng et al. reports high-intensity acoustic emission signals during corrosion processes suggesting their potential for determining the extents of corrosion and aiding in maintenance decisions [44]. Then also, a study by Chen et al., illustrated how acoustic emission technique may be used to monitor surface wear and track local corrosion occurrences while integrating data gathering systems for improved accuracy in structural health assessments [45]. Ma et al., on the other hand made another important addition by outlining the benefits of acoustic emission monitoring in differentiating acoustic signals from corrosion-related cracks and other structural sounds [46]. These studies exhibit how well AE Monitoring works as a proactive, non-invasive technique for managing corrosion in solar panel installations, which eventually results in more environmentally friendly energy options.

Fig.  5. Acoustic wave propagating due to stress corrosion cracking [47]

Solar Panel Corrosion Control

There are currently various methods corrosion of solar panel are controlled to ensure longevity and reliability. Below are discussed some of the methods deployed and solar panel corrosion control.

Encapsulation and protective coating

Encapsulation and Protective coatings are important method used to stop deterioration brought on by external elements like dust, moisture, and UV rays [48]] [49]. Ethylene Vinyl Acetate (EVA) is the most widely used as encapsulating substance in the solar panel manufacturing business [50] [51]. The developments in protective nano coatings significantly improve photovoltaic (PV) modules' longevity [52] and effectiveness [53], especially with regard to corrosion resistance [54].

The Role of Ethylene Vinyl Acetate (EVA) as an Encapsulant

Ethylene Vinyl Acetate is popular for its use as a copolymer which offers superior weather resistance, great optical clarity, and strong adherence to glass and solar cells [55]. It’s capacity to form a hermetic seal is essential because it preserves electrical insulation while shielding delicate solar cells from oxidative damage, moisture, and dust [56].

Numerous studies highlight the benefits of Ethylene Vinyl Acetate in encapsulation; for example, it is reported that approximately 80% of Photovoltaic modules use Ethylene Vinyl Acetate for encapsulation due to it favorable properties which includes good light transmittance, high adhesion levels to glass and back sheets [57]. Additionally, an investigation revealed that Ethylene Vinyl Acetate encapsulation creates a shield that significantly reduces the water vapor transmission rate (WVTR), protecting the solar cells  [58]; however, research also identifies the drawbacks of Ethylene Vinyl Acetate, specifically its vulnerability to UV degradation, which requires the use of UV-resistant protective glass to reduce degradation risks [59].

The relationship between the lamination parameters and the long-term durability of Ethylene Vinyl Acetate encapsulated modules has been highlighted in recent research that have investigated the lamination techniques employed in the encapsulation process [60] [61]. More specifically, research indicates that improving the longevity of solar modules requires ideal lamination conditions, such as suitable temperatures and curing durations [60]. The chemical stability and performance of the modules over time were found to be influenced by variables such as gel content, adhesion strength, and resistance to hydrolysis for EVA cured under different conditions [62].

Impact of Nano Coatings on Corrosion Mitigation

Hydrophobic nano coatings prevent moisture accumulation and repel dirt and dust, hence mitigating risk corrosion risk [63].

In certain studies, solar panels' lifespan and efficiency can be significantly increased by using nano coatings. One study, for example, showed that applying a self-cleaning nano-coating improved maximum power output by 65.2% and short-circuit current by 64.7% when compared to uncoated panels [53]. The capacity of the coating to lessen dust collection, which has a direct impact on light absorption efficiency, was credited with this notable performance improvement [64]. Again, hydrophilic nanocoating’s enhance self-cleaning systems and reduce the negative effects of soiling on solar panel performance [14]. According to one experimental study, silicon dioxide coatings efficiently protect PV cells from moisture exposure and UV rays, which is crucial for increasing their operational lifespan [65]. To improve adhesion and chemical stability of encapsulated systems nanotechnology has been used, according to [66] by using nano-coating materials with anti-corrosive qualities, weather resistance was accomplished.

The consequences of green nanoparticles on the environment and human health are likewise not uniformly regulated, nor are there standard testing methods [67] . Superhydrophobic coatings may not be able to be used practically due to problems with the surface's low mechanical stability [68]. Some drawbacks of organic coatings include poor adherence, coating permeability, and high temperatures [69].  Setbacks with EVA application may be improved by applying moisture resistive barriers over EVA films or exploring alternative encapsulant materials such as selica-gel or silicon-based material [70] [71].  Again, increasing coatings' mechanical stability and longevity is key. Techniques may include creating novel formulations that retain their qualities under stress, adding self-healing ingredients, and enhancing the coating's adherence to substrates [72].

Use of corrosive -Resistant Material

Alloying

Alloying has always shown to be one important option when it comes to developing a corrosive resistive material [81]. Manufacturers produce materials with better mechanical qualities and less corrosion susceptibility by mixing various metals, especially aluminum, with specialized alloying elements like silicon, magnesium, and zinc [82] [83] [84].  About 35% of the solar absorber are made of aluminum [85] [86] [87]. Research by Elbakhshwan et al. (2019), investigated the corrosive resistive nature of Inconel alloy in solar salt. Superficial nickel-based alloy (NI625) tested in molten solar salt consisting of 60 wt% NaNO3, 40 wt% KNO3, at 600 °C and for durations of 1000, 2000, 3000 and 4000 h [88]. Mass change data showed that the IN625 had the most resistance to corrosion with the lowest mass change and a more parabolic change indicating further resistance to long term corrosion. Rodríguez-Diaz et al., studied how aluminum-silicon-magnesium alloys corroded in saline environments. This research revealed that the alloys outperformed conventional aluminum, exhibiting a 30% reduction in corrosion rates. The synergistic impact of alloying process’s created a stronger coating of aluminum oxide [89]. In a different study, Investigation of the efficiency of zinc as an alloying element in aluminum for solar panel applications [90]. Their findings demonstrated a significant decrease in corrosion rates, which they attributed to zinc's galvanic protection, strengthening the alloy's resistance in marine conditions where electrolytic corrosion is common [91] [92].

Galvanic corrosion is one of the possible setbacks of alloy application. This is as a result of localized corrosion failures when dissimilar metals are bonded [93] [94]. By selecting materials carefully and combination metals that are near to each other in the galvanic series, this risk can be reduced [95][96]. Furthermore, surface treatments like anodizing can improve aluminum alloys' protective qualities even more [97].

Low-Iron Glass

Low-iron glass has exceptional optical qualities and resistance to corrosion [73], these qualities have made it a popular choice for solar panel applications  [74]. The lower iron level of low-iron glass ensures solar cells receive the ideal amount of sunlight for energy conversion, which minimizes coloring and maximizes light transmission [73] [75]. Additionally, it’s smoother surface makes it easier to prevent dust and grime buildup which can worsen corrosion and efficiency losses [76]. Susemihl and Dauwalter [77] discussed the benefits of using low-iron glass combined with silver reflective layers for solar applications. They reported the robustness and environmental stability of these mirrors. In the experiment, 4 mm low-iron glass was used with silver as the reflecting layer and appropriate protective layers. An initial reflectance of 94% can be maintained during its useful life, even under harsh conditions prevalent in solar applications. It can be argued that, using low-iron glass can aid with the longevity and dependability of solar reflectors by maintaining high reflectance and opposing environmental factors that could lead to corrosion [78]. However low-iron glass is more expensive than ordinary glass which is one of the challenges encountered [79]. Low-iron glass exhibit the same surface hardness and to abrasion as standard clear glass, which can impact its protective qualities [80]. Manufacturers can use surface treatments or coatings that promote improved weathering stability and scratch resistance to increase longevity [81] [82].

Electrically Conductive Adhesives (ECAs)

Electrically conductive adhesives (ECAs) offer a flexible way for mitigating corrosion in solar panels [83] [84]. They are created from using polymers with embedded metal fillers, such as copper, silver, or nickel, which give both electricity conductivity ability and strong adhesive properties [85] [86] [87]. ECAs are specifically beneficial because they can cure at lower temperatures [88] when bonding with sensitive electronic components than traditional soldering methods [89], avoiding potential heat destruction [90]. Studies again has proven that using ECAs in solar cells assembly improves net reliability by streamlining the manufacturing process [91], reducing the number of thermal cycles that components endure [92]. According to a study, ECAs demonstrated reduced contact resistivity and long-term electrical performance, both of which are critical for the long-term operation of solar modules [93] [94]. Eikelboom et al. (2002) did a study on warping and breaking of soldering and conductive adhesives [95].  In the experiment conductive adhesives showed that tremendous characteristics warping can be prevented and 80/spl mu/m thin cells do not break during and after interconnection. Contact resistance was same for both soldering and ECA. Damp/heat tests exhibited no deterioration after 2500 hours at 85/spl deg/C/85% humidity. After 200 cycles, temperature cycling -40/+80/spl deg/C has showed on effect. According to a study, ECAs demonstrated reduced contact resistivity [96] and long-term electrical performance, both of which are critical for the long-term operation of solar modules [97].

It was concluded that Conductive adhesives are a potential technology that reduces stress by combining low process temperatures, endurance, strong conductivity, and outstanding mechanical qualities [85] [98].  Enhancements can be made by creating ECAs with optimized filler geometries and polymer mixes, which retain electrical conductivity while improving mechanical qualities [99] [100]. The environment in which the panels will be installed, and the application techniques used must be carefully considered in order to provide strong adhesion under a range of operational pressures.

Environmental Control and Monitoring

Integrated sensor systems and climate-specific solar panel placement are two efficient ways that contribute to corrosion prevention in solar panels through environmental monitoring.

Integrated sensor systems

Real time monitoring of ambient conditions and corrosion levels in solar panels has been achieved through recent advancements in integrated sensor systems [101] [102]. Useful data that are imperative for decision-making on maintenance and the application of corrosion prevention methods are offered by these sensors [103].

Sarkar et al., did a study on the application of Internet of Things (IoT)-based wireless sensor network (WSN) to track the performance of low-power rooftop photovoltaic (PV) panels [104].The study revealed that operational effectiveness of small-scale photovoltaic installation can be achieved through effective monitoring systems. The authors emphasized that the use of wireless sensor network can aid the assessment of productivity, efficiency, and overall system performance, facilitating easier calculation and analysis. Qiao et al., discussed a noteworthy study by Kumar, were integrated sensor system created specially for tracking the rate of corrosion in reinforced concrete structures housing solar panels was investigated [105]. In the discussion, result from the study showed A customized proof-of-concept system utilizing a wireless sensor network (WSN) was developed by Kampman et al. [106]. This system was used to monitor corrosion in water pipelines with electrochemical sensor integration to monitor and detect corrosion levels and give real-time data facilitating timely maintenance. According to the publication, the need for manual inspection was lowered due to the implementation of wireless network system. It proved continuous monitoring, allowing for early detection of material deterioration for timely mediation and safety of infrastructure. The publication "Batteryless Environmental Sensing for Sustainable Corrosion Monitoring" by Pappinisseri Puluckul and Weyn [107], introduces a unique way to corrosion monitoring by building a battery-free environmental sensing system. Their system relay on energy harvesting techniques, including thermoelectric generation from soil-air temperature differences to power sensors that monitor environmental parameters like humidity, ambient temperature, and soil temperature. The incorporation of energy harvesting technologies, as shown in Liu et al.'s study, improves the sustainability and longevity of wireless sensor network by eliminating the dependence on batteries, thus supporting more efficient and eco-friendly corrosion monitoring systems [108]. Despite the success in deploying wireless sensor network in corrosion detection, there are key challenges that are encountered because of short battery life of sensor [109]. To add, setbacks due to the intricacy of integrating data [110] from numerous monitoring devices are also faced. To ensure long-term dependability and lessen the need for battery replacements [111] [112] [113], further studies should concentrate on creating self-sufficient systems that use renewable energy sources.

Climate-Specific Solar Panel Siting

Climate change is known to impact solar panels in many ways, for that reason solar panel placement is crucial in reducing corrosion concerns [114] [115] [116]. The negative impacts of weather and geographic circumstances on solar panels can be considerably reduced with proper location [117] [118]. Elevated temperatures and prolonged moisture promote encapsulant degradation in hot, humid tropical environments. This accelerates encapsulant breakdown and increases acetic acid emission, which in turn increases aggressive metal dissolution and migration conditions [182].

A study by Sousa et al., investigated the potential effects of climate change on the corrosion of structures, especially those essential to solar installations [119]. The experiment illustrates the importance of incorporating climate modeling into the design process. This facilitates in forecasting the long-term performance and reducing corrosion hazards related to particular weather patterns. The study proposes that awareness of regional climate variances required to create customized design guidelines that can improve the robustness and effectiveness of solar systems. The International Energy Agency Photovoltaic Power Systems Program replication titled “Climatic Rating of Photovoltaic Modules", emphasize the need for integrating site-specific climate data into photovoltaic installation design. The research demonstrates how adaptive photovoltaic module selection and system design that suits local climatic conditions can significantly increase energy yield and system dependability. This is achieved by examining operational data from photovoltaic systems across different climate zones. The results support the strategy of including thorough climatic analyses in the planning phase, which guarantees solar installations are tailored to their settings and enhances longevity and overall performance [120]. Article by Ronald stated the need to select solar panels that comply with International Electrotechnical Commission (IEC) 61701 standard when considering setting up in coastal regions. Due to the abundance of sea salt in the region, the standard provided confidence in the solar panel’s ability to resist corrosive effect. Homeowners and installer can mitigate the chance of corrosion and improve solar panel lifespan and functionality of solar installation in these types of climates by selecting panels that fulfill this certification [121] [122].

Notwithstanding these observations, a drawback identified in all of these research is the generalizability of results across diverse geographic locations, which could result in conflicting outcomes when criteria are modified for other contexts [123] [124] [125]. In order to help with more informed site selection, future research should concentrate on creating an extensive database on corrosion affects specific to various regional conditions [126] [127] [128].

Advanced Testing and Validation

Advanced Testing

Advanced testing technique play a crucial part in detecting and computing corrosion in solar panels [129] [130]. These methods used accelerated aging testing where real-world environmental conditions are simulated to provide assessments of corrosion susceptibility [131] [132][ [133].

Copper-accelerated acetic acid salt spray (CASS) which has surfaced as a novel accelerated corrosion test was used in a study to examine the longevity of supporting components in floating photovoltaic systems (FPS) [160]. This technique exposed materials to extremely corrosive environment in order to access its resilience to deterioration. This approach mimics of the harsh conditions that photovoltaic modules may experience especially in coastal or marine regions [161]. This kind of accelerated testing is used a valuable predictive tool for judging the lasting performance of different materials in certain environments [134]. Additionally, researchers from Panasonic's Sanyo subsidiary demonstrated a connection between damp-heat (DH) testing and field exposure for electrode corrosion in PV modules [135]. Damp-heating testing is a type of accelerated aging testing where PV modules are placed in controlled chambers with high temperature and humidity (85°C and 85% relative humidity) for prolonged periods (at least 1,000 hours) [135] [136]. By using this method, module durability can be predicted without having to wait for actual degradation over several years [137] [138]. There are setbacks while using accelerated aging testing and validation [139] [140] [15,16]. Weiß et al., emphasizes the limitations of accelerated aging tests for photovoltaic (PV) modules, indicating that these tests often focus on stress factors like humidity or temperature, alluding to capture the collective effect of real-world environmental situations [132]. Consequently, the actual degradation rates values are either overestimate or underestimate [132] [141]. Gunther, M. J.), found the same to be the case of validation in his experiment Design and Validation of a Led-Based Solar Simulator for Solar Cell and Thermal Testing [139].

Validation

Validation is a technique that is used as a testing complementary for addressing ambiguity in the functioning and dependability of solar panel material and structure [142] [143]. Validation is performed through standardized procedures to ensure manufacturers meet industrial requirements [144] [145].

Böök et al, (2020), created a new direct normal irradiance (DNI) quality control method which is a validation technique to improve the reliability and longevity of solar panel, which was imperative for PV modeling [146]. The validation consisted of analyzing outputs of model vs actual performance data placed in high latitude [142].  The outcomes of the experiment denoted that featuring the direct normal irradiance quality control method enhanced the model's precision, indicating predictions that are more dependable for photovoltaic (PV) system performance in these regions [147]. Again, validation was used by Migliorini et al. (2017) when experimental test was performed on a photovoltaic system by collecting data on variables such as irradiance, temperature, and electrical output [148].  They then compared the simulated measurement with the empirical data to demonstrated accuracy of information. A validation procedure, which illustrated significant connection between the model's predictions and the experimental data was used to confirm model's accuracy in forecasting photovoltaic (PV) module performance in dynamic situations. Lisbona, E. F. (2003), used various validation method to ensure reliability and performance of solar cell in space application [177]. The validation method involved testing done mainly to predict the endurance of solar array versus parameters such as radiations, mechanical stress, and extreme temperature. These assessments are critical for detecting probable degradation mechanisms or corrosion that could negatively impact the structural reliability and efficiency of solar cells in space [149] [150].

Design and Structural Modifications

Material Selection and coating system

Selecting a material that is corrosive resistance is an important aspect of solar panel design [151] [152]. Work has been done to predict that; some materials can resist corrosion more than the others when constructing solar panel [153] [154].

For instance, research has shown that stainless steel demonstrated greater resistance to corrosion contrast to traditional galvanized steel [155] [156], subsequent showing significant improvement in the structural integrity and durability of the solar installations [157]. Conspicuously, the application of coatings on aluminum structures situated in coastal environments decreased corrosion rates by up to 50% [158]

Structural Reinforcements

Structural modifications are fundamental for inhibiting corrosion-induced failures in solar panels, especially reinforcements in mounting systems [159]. Correct structural design can enhance load-bearing capacities, enabling stability whereas reducing exposure to corrosive environment [160].

Fang et al. (2019), dives in the utilization of fiber reinforced polymer (FRP) composites in civil infrastructure, focusing on their applications in hostile conditions [161]. The study highlighted the intrinsic benefits of fiber reinforced polymer composites, which includes greater resistance to corrosion, making them more desirable for structural applications than traditional materials. The author also presented applications of fiber reinforced polymer composites in civil infrastructure, including truss and frame structures in high humidity areas, floating structures for solar panels etc. In another research performed by Hu et al., structural reinforcement was used to optimize performance and functionality of concentrated photovoltaic panel (CPP) structure built for integration into pavement systems [181]. After rigorous testing, the optimized structure met the optimum requirement. The work showed that the concentrated photovoltaic panel which was used for structural reinforcement was imperative for structural integrity.  The implementation of structural reinforcements can encounter constraints related to cost and material availability. While hybrid systems offer better performance, their higher costs may pose barriers to widespread adoption [162].

Design Configuration

Novel design configurations for solar panels have appeared to be good solutions to minimize corrosion [163] [164]. Strategic positioning and panel spacing can lessen pooling of water and moisture retention on panel surface, which are noteworthy corrosion contributors [165].

Research suggests that placing the panel at an optimum angle with respect to the local climate is fundamental for inhibiting excessive gathering of moisture on solar panels [166] [167] [168]. In other studies, researchers found a sizable reduction in rate of corrosion up to 30% by just changing tilt angles [169] [170]. The results highlight the significance of altering solar panel installations to fit a specific climatic setting of a site to curtail corrosion risks. Again, elevation mounting of solar panel [171] is one of the techniques that may be used to prevent corrosion of solar panel. It reduces exposure to moisture, soil, and debris that can accelerate material degradation [172]. Elevation mounting of solar panel enables faster drying, thereby reducing the probability of corrosion by improving airflow around the panel [173] [174]. Again, elevation mounting of solar panel is one of the techniques that may be used to prevent corrosion of solar panel. It reduces exposure to moisture, soil, and debris that can accelerate material degradation [175]. Elevation mounting of solar panel enables faster drying, thereby reducing the probability of corrosion by improving airflow around the panel [176] [177]. Additionally, water collection inside the structural components is inhibited by this technique [178], this inhibition is critical because confined moisture can worsen the internal corrosion [176]. Elevation approaches is necessary for sustaining the structural reliability and durability of solar installations [179] [180]. A familiar limitation of design configurations is the dependence on regional meteorological data for ideal performance. The fluctuations in environmental factors across different regions can make difficult the application of generalized design suggestions [181] [29,30].

Conclusion

Corrosion in solar photovoltaic systems remains a critical challenge due to its direct impact on system durability, efficiency, and long-term maintenance costs. Significant progress has been achieved in corrosion detection and prevention through advances in monitoring techniques, protective coatings, material selection, and structural design modifications. However, limitations related to cost, environmental variability, monitoring complexity, and the lack of universally adopted standards continue to constrain the effectiveness of current mitigation strategies.

Effective corrosion management therefore requires an integrated approach that combines corrosion-resistant materials, advanced protective technologies, and proactive maintenance practices tailored to specific environmental conditions. Emerging research highlights several key priorities for strengthening corrosion resilience in photovoltaic systems, including the development of novel materials and multifunctional coatings, improved alignment between accelerated laboratory testing and real-world field performance, and the integration of real-time diagnostic and predictive maintenance systems. In addition, the establishment of comprehensive and standardized corrosion characterization protocols that link microstructural degradation to field performance is essential for improving comparability across studies and guiding durable system design. Addressing these research gaps will be crucial to enhancing long-term reliability, reducing lifecycle costs, and ensuring the sustainability of solar energy systems deployed across diverse climatic regions. [183]

Ethical Compliance: All procedures performed in studies involving human participants were in accordance with the ethical standards of the institutional and/or national research committee and with the 1964 Helsinki Declaration and its later amendments or comparable ethical standards.

The authors declare that they have no affiliations with or involvement in any organization or entity with any financial interest in the subject matter or materials discussed in this manuscript.

Disclaimer (Artificial intelligence)

Author(s) hereby declare that NO generative AI technologies such as Large Language Models (ChatGPT, COPILOT, etc.) and text-to-image generators have been used during the writing or editing of this manuscript.

REFERENCES

| [1] | D. C. Jordan, T. J. Silverman, J. H. Wohlgemuth, S. R. Kurtz and K. T. VanSant, "Photovoltaic failure and degradation modes," Prog. Photovolt Res. Appl, pp. 25, 318-326, 2017. |
| --- | --- |
| [2] | J. H. Kim, J. Park, D. Kim and N. Park, "Study on Mitigation Method of Solder Corrosion for Crystalline Silicon Photovoltaic Modules," Int. J. Photoenergy 2014, 2014. |
| [3] | J. Li, Y. C. Shen, P. Hacke and M. Kempe, "Electrochemical mechanisms of leakage-current-enhanced delamination and corrosion in Si photovoltaic modules," Sol. Energy Mater. Sol. Cells, pp. 188, 273-279, 2018. |
| [4] | G. Oreski, A. Rauschenbach, C. Hirschl, M. Kraft, G. C. Eder and G. Pinter, "Crosslinking and post-crosslinking of ethylene vinyl acetate in photovoltaic modules," J. Appl. Polym. Sci. , pp. 1324, 44912, 2017. |
| [5] | W. A. Czanderna and F. J. Pern, "Encapsulation of PV Modules Using Ethylene Vinyl Acetate Copolymer as a Pottant: A Critical Review," Sol. Energy Mater. Sol. Cells , pp. 43, 101-181, 1993. |
| [6] | N. Kim, S. Lee, X. G. Zhao, D. Kim, C. Oh and H. Kang, " Reflection and durability study of different types of backsheets and their impact on c-Si PV module performance," Sol. Energy Mater. Sol. Cells, pp. 146, 91–98, 2016. |
| [7] | A. Omazic, G. Oreski, M. Halwachs, G. C. Eder, C. Hirschl, L. Neumaier, G. Pinter and M. Erceg, "Relation between degradation of polymeric components in crystalline silicon PV module and climatic conditions: A literature review," Sol. Energy Mater. Sol. Cells , pp. 192, 123–133, 2019. |
| [8] | A. Kraft, L. Labusch, T. Ensslen, I. Dürr, J. Bartsch, M. Glatthaar, S. Glunz and H. Reinecke, "Investigation of Acetic Acid Corrosion Impact on Printed Solar Cell Contacts," IEEE J. Photovolt, pp. 5, 736-743, 2015. |
| [9] | G. Oreski, A. Omazic and B. Ottersböck, "Degradation processes and mechanisms of encapsulants. In Durability and Reliability of Polymers and Other Materials in Photovoltaic Modules," William Andrew Publishing., pp. 135-152, 2019. |
| [10] | A. Badiee, "An examination of the response of ethylene-vinyl acetate film to changes in environmental conditions (Doctoral dissertation, University of Nottingham).," 2016. |
| [11] | K. Kumba, P. Upender, P. Buduma, M. Sarkar, S. P. Simon and V. Gundu, "Solar tracking systems: Advancements, challenges, and future directions: A review," Energy Reports, pp. 12, 3566-3583., 2024. |
| [12] | M. Novak, R. Vohnout, L. Landkamer, O. Budik, , M. Eider and A. Mukherjee, "Energy-efficient smart solar system cooling for real-time dynamic weather changes in mild-climate regions," Renewable and Sustainable Energy Reviews, , pp. 182, 113347, 2023. |
| [13] | X. Hou, Z. Li and Z. Zhang, "Selectively producing acetic acid via boric acid-catalyzed fast pyrolysis of woody biomass. Catalysts,," pp. 11(4), 494, 2021. |
| [14] | M. D. Kempe, G. J. Jorgensen, K. M. Terwilliger, T. J. McMahon, C. E. Kennedy and T. T. Borek, "Acetic Acid Production and Glass Transition Concerns with Ethylene-Vinyl Acetate Used in Photovoltaic Devices," Solar energy materials and solar cells, pp. 91 (4), 315–329, 2007. |
| [15] | S. Kaplanis and E. Kaplani, "Energy performance and degradation over 20 years performance of BP c-Si PV modules. Simulation Modelling Practice and Theory,," pp. 19(4), 1201-1211., 2011. |
| [16] | A. Azizi, P. O. Logerais, A. Omeiri, A. Amiar, A. Charki, O. Riou and J. F. Durastanti, "Impact of the aging of a photovoltaic module on the performance of a grid-connected system.," Solar Energy, pp. 174, 445-454, 2018. |
| [17] | H. Xiong, C. Gan, X. Yang, Z. Hu, H. Niu, J. Li, J. Si, P. Xing and X. Luo, " Corrosion behavior of crystalline silicon solar cells," Microelectron. Reliab, pp. 70, 49–58, 2017. |
| [18] | S. Szabo and L. Bakos, "Cathodic protection with sacrificial anodes. Corrosion Reviews," pp. 24(3-4), 231-280., 2006. |
| [19] | T. E. Graedel and R. P. Frankenthal, "Corrosion mechanisms for iron and low alloy steels exposed to the atmosphere.," Journal of the Electrochemical Society, pp. 137(8), 2385, 1990. |
| [20] | P. T. Vianco, "Corrosion issues in solder joint design and service (No. SAND99-3034J). Sandia National Lab.(SNL-NM), Albuquerque, NM (United States); Sandia National Lab.(SNL-CA), Livermore, CA (United States).," 1999. |
| [21] | A. De Rose, A. Kraft, S. Gledhill, M. T. Ali, C. Pscherer and U. Eitner, "Solder interconnection of aluminum foil rear side metallization for passivated emitter and rear solar cells.," in In 7th Workshop on Metallization and Interconnection for Crystalline Silicon Solar Cells., 2017. |
| [22] | D. Balageas, X. Maldague, D. Burleigh, V. P. Vavilov, B. Oswald-Tranta, J. M. Roche and G. M. Carlomagno, "Thermal (IR) and other NDT techniques for improved material inspection," Journal of nondestructive evaluation, pp. 35, 1-17, 2016. |
| [23] | M. A. Akhloufi, Y. Guyon, C. I. Castanedo and A. Bendada, "Three-dimensional thermography for non-destructive testing and evaluation," Quantitative InfraRed Thermography Journal, pp. 14(1), 79-106, 2017. |
| [24] | A. Kylili, P. A. Fokaides, P. Christou and S. A. Kalogirou, "Infrared thermography (IRT) applications for building diagnostics: A review," Applied Energy,, pp. 134, 531-549, 2014. |
| [25] | J. A. Tsanakas, L. Ha and C. Buerhop, "Faults and infrared thermographic diagnosis in operating c-Si photovoltaic modules: A review of research and future challenges," Renewable and sustainable energy reviews, pp. 62, 695-709, 2016. |
| [26] | C. Buerhop, L. Bommes, J. Schlipf, M. Pickel, A. Fladung and I. Peters, "Infrared imaging of photovoltaic modules: a review of the state of the art and future challenges facing gigawatt photovoltaic power stations," Progress in Energy, pp. 4(4), 042010, 2022. |
| [27] | A. W. Kandeal, M. R. Elkadeem, A. K. Thakur, G. B. Abdelaziz, R. Sathyamurthy, A. E. Kabeel and S. W. Sharshir, "Infrared thermography-based condition monitoring of solar photovoltaic systems: A mini review of recent advances," Solar Energy, pp. 233, 33-34, 2021. |
| [28] | S. Gallardo Saavedra, "Detection, classification and characterization of defects in photovoltaic modules through the use of thermography, electroluminescence, IV curves and visual analysis," 2020. |
| [29] | L. Hernández-Callejo, S. Gallardo-Saavedra, M. D. Alonso-Garcia, J. Muñoz-Cruzado-Alba and J. Ballestín-Fuertes , "Infrared thermography for the detection and characterization of photovoltaic defects: comparison between illumination and dark conditions," Sensors, pp. 20(16), 4395, 2020. |
| [30] | J. Ballestín-Fuertes, J. Muñoz-Cruzado-Alba, J. F. Sanz-Osorio, L. Hernández-Callejo, V. Alonso-Gómez, J. I. Morales-Aragones and A. Moretón-Fernández, "Novel utility-scale photovoltaic plant electroluminescence maintenance technique by means of biodirectional power inverter controller.," Applied Science , pp. 10(9), 3084, 2020. |
| [31] | J. I. Morales-Aragonés, S. Gallardo-Saavedra, V. Alonso-Gómez, F. J. Sánchez-Pacheco, M. A. González, O. Martínez and L. Hernández-Callejo, "Low-cost electronics for online iv tracing at photovoltaic module level: Development of two strategies and comparison between them," Electronics , pp. 10(6), 3084, 2021. |
| [32] | H. S. Magar, R. Y. Hassan and A. Mulchandani, "Electrochemical impedance spectroscopy (EIS): Principles, construction, and biosensing applications," Sensors, pp. 21(19), 6578., 2021. |
| [33] | T. K. Bera, "Electrical impedance spectroscopy (EIS) for photovoltaic materials: possibilities and challenges. In IOP Conference Series:," Materials Science and Engineering, vol. 955, pp. No. 1, p. 012076, 2020. |
| [34] | V. Encinas-Sánchez, M. T. De Miguel, M. I. Lasanta, G. García-Martín and F. J. Pérez, "Electrochemical impedance spectroscopy (EIS): An efficient technique for monitoring corrosion processes in molten salt environments in CSP applications," Solar energy and solar cell, pp. 191, 157-163, 2019. |
| [35] | B. Pejcic and R. De Marco, "Impedance spectroscopy: Over 35 years of electrochemical sensor optimization," Electrochimica acta, pp. 51(28), 6217-6229., 2006. |
| [36] | V. Encinas-Sánchez, A. Macías-García, M. T. De Miguel, F. J. Pérez and J. M. Rodríguez-Rego, "Electrochemical impedance analysis for corrosion rate monitoring of sol–gel protective coatings in contact with nitrate molten salts for CSP applicatio," Materials, pp. 16(2), 546, 2023. |
| [37] | P. Wang, K. Du, H. Yin and D. Wang, "Corrosion and protection of metallic materials in molten carbonates for concentrating solar power and molten carbonate electrolysis applications.," Corrosion Communications, pp. 11, 58-71., 2023. |
| [38] | L. González-Fernández, A. Anagnostopoulos, T. Karkantonis, S. Dimov, M. Chorążewski, Y. Ding and Y. Grosu, "Laser-texturing of stainless steel as a corrosion mitigation strategy for high-temperature molten salts applications under dynamic condition," Solar Energy Materials and Solar Cells, pp. 257, 112380, 2023. |
| [39] | D. K. Hwang, B. Lee, D. H. Kim and R. P. Chang, "Efficiency enhancement in dye-sensitized solar cells by three-dimensional photonic crystals," Applied Physics Express, , pp. 5(12), 122301, 2012. |
| [40] | X. Li, "A brief review: acoustic emission method for tool wear monitoring during turning," International Journal of Machine Tools and Manufacture, pp. 42(2), 157-165., 2002. |
| [41] | K. Ono, "Review on structural health evaluation with acoustic emission.," Applied Sciences, pp. 8(6), 958, 2018. |
| [42] | X. Chen and B. Li, "Acoustic emission method for tool condition monitoring based on wavelet analysis," The International Journal of Advanced Manufacturing Technology, pp. 33, 968-976, 2007. |
| [43] | N. Angelopoulos and V. Kappatos, "An Experimental Assessment Using Acoustic Emission Sensors to Effectively Detect Surface Deterioration on Steel Plates.," Sensors, pp. 24(19), 6462., 2024. |
| [44] | Q. Geng, H. Li and Y. Li, "Dynamic and acoustic response of a clamped rectangular plate in thermal environments: experiment and numerical simulation," The Journal of the Acoustical Society of America, pp. 135(5), 2674-2682., 2014. |
| [45] | L. Chen, G. Bi, X. Yao, J. Su and C. Tan, "Feng, W., ... & Moon, S. K. (2024). In-situ process monitoring and adaptive quality enhancement in laser additive manufacturing: a critical review," Journal of Manufacturing Systems,, pp. 74, 527-574., 2024. |
| [46] | S. Ma, S. Ren, Z. Chen, C. Wu and S. Jiang, "Wooden beam damage evaluation under bending loading based on the integration of acoustic emission and principal component analysis.," Measurement, pp. 222, 113569, 2023. |
| [47] | L. Calabrese and E. Proverbio, "A review on the applications of acoustic emission technique in the study of stress corrosion cracking.," Corrosion and Materials Degradation, pp. 2(1), 1-30, 2020. |
| [48] | Diamond Fusion Protective, "Solar Panel Protective Coating". |
| [49] | M. D. Kempe, "Control of moisture ingress into photovoltaic modules," in Conference Record of the Thirty-first IEEE Photovoltaic Specialists Conference, 2005, 2005. |
| [50] | Solar encapsulation market, "Solar Encapsulation Market by Material (EVA, PVB, PDMS, Ionomer, TPU, Polyolefin), Technology (Crystalline Silicon, Thin-film Solar), Application (Ground-mounted, Building-integrated Photovoltaic, Floating Photovoltaic) & Region - Global Forecast to 2028," Solar encapsulation market, 2024. |
| [51] | H. K. Trivedi, A. Meshram and R. Gupta, "Removal of encapsulant Ethylene-vinyl acetate (EVA) from solar cells of photovoltaic modules (PVMs).," Materials Today: Proceedings,, pp. 112, 73-76, 2024. |
| [52] | Institute of Corrosion, "The Advancing Role of Nano-Coatings in Corrosion Protection". |
| [53] | A. Ahmed, M. Elsakka, Y. Elhenawy, A. Amer, A. Mansi, M. Bassyouni and A. Refaat, "Experimental investigation of a nano coating efficiency for dust mitigation on photovoltaic panels in harsh climatic conditions," 2024. |
| [54] | L. M. Shaker, A. Alamiery and W. N. R. W. Isahak, "Corrosion in solar cells: challenges and solutions for enhanced performance and durability," Journal of Optics, pp. 1-15, 2023. |
| [55] | D. D. Rooij, "EVA (ethylene vinyl acetate) Film: composition and application.," SINO VALTAICS, 2011. [Online]. Available: https://sinovoltaics.com/learning-center/materials/ethylene-vinyl-acetate-eva-film-composition-and-application/. [Accessed 06 03 2025]. |
| [56] | RenewSys India. , " EVA v/s POE: A Comparative Study of Solar Panel Encapsulants.," RenewSys India. , 2024. [Online]. Available: https://www.renewsysworld.com/post/eva-v-s-poe-a-comparative-study-of-solar-panel-encapsulants. [Accessed 22 02 2025]. |
| [57] | S. Jiang, K. Wang, H. Zhang, Y. Ding and Q. Yu, "Encapsulation of PV modules using ethylene vinyl acetate copolymer as the encapsulant," Macromolecular Reaction Engineering, pp. 9(5), 522-529, 2015. |
| [58] | F. Corsini and G. Griffini, "Recent progress in encapsulation strategies to enhance the stability of organometal halide perovskite solar cells.," Journal of Physics: Energy, pp. 2(3), 031002., 2020. |
| [59] | A. L. Andrady, A. M. Heikkilä, K. K. Pandey, L. S. Bruckman, C. C. White, M. Zhu and L. Zhu, "Effects of UV radiation on natural and synthetic materials," Photochemical & Photobiological Sciences, pp. 22(5), 1177-1202, 2023. |
| [60] | D. Wu, P. Wessel, J. Zhu, D. Montiel-Chicharro, T. R. Betts, A. Mordvinkin and R. Gottschalg, "Influence of lamination conditions of EVA encapsulation on photovoltaic module durability.," Materials,, pp. 16(21), 6945., 2-23. |
| [61] | M. Landa-Pliquet, T. Béjat, M. Serasset, A. Descormes, E. Mofakhami and E. Voroshazi, "Enhancing photovoltaic modules encapsulation: Optimizing lamination processes for Polyolefin Elastomers (POE) through crosslinking behavior analysis," Solar Energy Materials and Solar Cells , pp. 267, 112725, 2024. |
| [62] | L. Gnocchi, A. Virtuani, A. Fairbrother, E. Annigoni and C. Ballif, "The effect of storage conditions on the long-term stability of ethylene-vinyl-acetate (EVA) copolymer used in glass/glass modules," Solar Energy Materials and Solar Cells, pp. 262, 112526, 2023. |
| [63] | T. T. Mohammed, H. K. Judran and S. R. Faraj, "Preparation and characterization of SiO2 nanocoating for self-cleaning solar panels," in In AIP Conference Proceedings (Vol. 3002, No. 1). AIP Publishing., 2024. |
| [64] | S. Z. Said, S. Z. Islam, N. H. Radzi, C. W. Wekesa, M. Altimania and J. Uddin, "Dust impact on solar PV performance: A critical review of optimal cleaning techniques for yield enhancement across varied environmental conditions," Energy Reports, pp. 12, 1122-1141, 2024. |
| [65] | Q. Yang, J. Cao, R. Ding, K. Zhan, Z. Yang, B. Zhao and V. Ji, "The synthesis and mechanism of superhydrophobic coatings with multifunctional properties on aluminum alloys surface: a review," Progress in Organic Coatings, p. 107875, 2023. |
| [66] | Q. Zhu, M. H. Chua, P. J. Ong, , J. J. C. Lee, K. L. O. Chin, S. Wang and X. J. Loh, "Recent advances in nanotechnology-based functional coatings for the built environment. Materials Today Advances, 15, 100270.," 2022. |
| [67] | J. Portugal, C. Bedia, F. Amato and A. T. Juárez-Facio, "Toxicity of airborne nanoparticles: Facts and challenges," Environment international, p. 108889, 2024. |
| [68] | H. Y. Erbil, "Practical applications of superhydrophobic materials and coatings: problems and perspectives," Langmuir, pp. 36(10), 2493-2509., 2020. |
| [69] | A. Hooda, M. S. Goyat, J. K. Pandey, A. Kumar and R. Gupta , " A review on fundamentals, constraints and fabrication techniques of superhydrophobic coatings," Progress in Organic Coatings, pp. 142, 105557, 2020. |
| [70] | R. Fairbrother, L. Gnocchi, C. Ballif and A. Virtuani, "Corrosion testing of solar cells: Wear-out degradation behavior," Solar Energy Materials and Solar Cells, pp. 248, 111974., 2022. |
| [71] | K. Aitola, G. Sonai, M. Markkanen, J. J. Kaschuk, X. Hou, K. Miettunen and P. D. Lund, "Encapsulation of commercial and emerging solar cells with focus on perovskite solar cells," Solar Energy, pp. 237, 264-283., 2022. |
| [72] | L. Li, J. Wei, J. Zhang, B. Li, Y. Yang and J. Zhang, "Challenges and strategies for commercialization and widespread practical applications of superhydrophobic surfaces," Science Advances, pp. 9(42), eadj1554. , 2023. |
| [73] | Gaudian glass, "low-iron-glass". |
| [74] | Cardinal Glass Industries, "The ultimate corrosion-resistant glass for railing infill applications.," 2022. |
| [75] | G. Dodd, "Manufacture and processing. In Construction Materials," CRC Press, pp. 433-446, (2017). |
| [76] | S. Xue, S. Yang, X. Li, Q. Li and B. Hu, "(2024). A comprehensive review on self-cleaning glass surfaces: durability, mechanisms, and functional applications," RSC advances, pp. 14(46), 34390-34414., 2024. |
| [77] | I. Susemihl and A. Dauwalter, "Silvered low-iron glass: experience and new developments.Transparent," in In Optical Materials Technology for Energy Efficiency and Solar Energy Conversion XI: Selective Materials, Concentrators and Reflectors, Transparent Insulation and Superwindows , 1992. |
| [78] | S. Caron, "Accelerated aging of thick glass second surface silvered reflectors under sandstorm conditions.," 2011. |
| [79] | HHG Glass Solution, "Low Iron Grass and Clear Glass". |
| [80] | Vitro Architectural Glass,, "Glass Education Center, Ensuring a True Low-Iron Look". |
| [81] | J. L. Pellegrino, " Energy and environmental profile of the US glass industry.," Energetics, Inc., Columbia, MD (United States)., 2020. |
| [82] | A. Duran, J. F. Navarro, P. Casariego and A. Joglar, "Optical properties of glass coatings containing Fe and Co.," Journal of Non-Crystalline Solids, pp. 82(1-3), 391-399, 1986. |
| [83] | M. Ayalasomayajula, M. R. Khurana and P. S. Chaudhary, "Electrically Conductive Adhesives in Microelectronics Packaging.," Journal of Electronic Packaging, p. 146(4)., 2024. |
| [84] | V. P. Vu and T. T. Phan, "Electrically Conductive Self-Healing Epoxy Composites for Flexible Applications: A Review. Energy Consumption, Conversion, Storage, and Efficiency.," 2023. |
| [85] | Y. G. Li, D. Lu and C. P. Wong, "Electrical conductive adhesives with nanotechnologies.," Springer Science & Business Media., 2009. |
| [86] | R. Gomatam and K. L. Mittal, " Electrically conductive adhesives," pp. 152-450. VSP, 2008. |
| [87] | K. George, A. Thomas, N. Shajimon, J. Joseph and R. Paul, "A review on electrically conductive adhesives in electronic packaging," Int. J. Res. Appl. Sci. Eng. Technol, pp. 9, 440-452., 2021. |
| [88] | H. K. Kim and F. G. Shi, "Electrical reliability of electrically conductive adhesive joints: dependence on curing condition and current density.," Microelectronics journal, pp. 32(4), 315-321., 2001. |
| [89] | G. Zeng, S. McDonald and K. Nogita, "Development of high-temperature solders.," Microelectronics Reliability, pp. 52(7), 1306-1322., 2012. |
| [90] | S. Menon, E. George, M. Osterman and M. Pecht, "High lead solder (over 85%) solder in the electronics industry: RoHS exemptions and alternatives.," Journal of Materials Science: Materials in Electronics, pp. 26, 4021-4030, 2015. |
| [91] | M. E. (. Karahallı, "Performance, Design, and Interconnection Optimization of Shingled Solar Cell for a Photovoltaic Module Application (Master's thesis, Middle East Technical University)," 2024. |
| [92] | V. Sharma and S. S. Chandel, "Performance and degradation analysis for long term reliability of solar photovoltaic systems: A review. Renewable and sustainable energy reviews," pp. 27, 753-767., 2013. |
| [93] | M. J. Yim , Y. Li, K. S. Moon, K. W. Paik and C. P. Wong, "Review of recent advances in electrically conductive adhesive materials and technologies in electronic packaging," Journal of adhesion science and technology, pp. 22(14), 1593-1630, 2008. |
| [94] | J. C. Jagt, "Reliability of electrically conductive adhesive joints for surface mount applications: a summary of the state of the art.," IEEE Transactions on Components, Packaging, and Manufacturing Technology: Part A, , pp. 21(2), 215-225., 2002. |
| [95] | D. W. K. Eikelboom, J. H. Bultman , A. Schonecker, M. H. H. Meuwissen, M. . A. J. C. Van Den Nieuwenhof and D. L. Meier, "Conductive adhesives for low-stress interconnection of thin back-contact solar cells," in In Conference Record of the Twenty-Ninth IEEE Photovoltaic Specialists Conference, 2002. |
| [96] | B. Adothu, S. Kumar, J. J. John, G. Oreski, G. Mathiak, B. Jäckel and R. Gottschalg, "Comprehensive review on performance, reliability, and roadmap of c‐Si PV modules in desert climates: A proposal for improved testing standard.," Progress in Photovoltaics: Research and Applications, pp. 32(8), 495-527., 2024. |
| [97] | M. Kronsbein, L. Böck,, K. Dyhr, T. Rößler and N. Willenbacher, "Less is More: Enabling Low-Filled Electrically Conductive Adhesives for Shingled Solar Cell Interconnection Using the Capillary Suspension Concept. Available at SSRN 5123528.". |
| [98] | R. Zhang, W. Lin, K. Lawrence and C. P. Wong, "(2010). Highly reliable, low cost, isotropically conductive adhesives filled with Ag-coated Cu flakes for electronic packaging applications," International journal of adhesion and adhesives, pp. 30(6), 403-40, 2010. |
| [99] | M. L. Clingerman, J. A. King, K. H. Schulz and J. D. Meyers, "Evaluation of electrical conductivity models for conductive polymer composites.," Journal of Applied Polymer Science, pp. 83(6), 1341-1356, 2002. |
| [100] | F. Zhang, N. Tang, Q. Jiang, K. Qi, X. Zhu, Z. Luo and B. Fang, "Progress in polyacrylate‐based electrically conductive adhesives: Featured properties, preparation, applications, and perspectives," Polymer Composites, pp. 45(7), 5781-5803., 2024. |
| [101] | S. Sivagamasundari and M. S. Rayudu, "IoT based solar panel fault and maintenance detection using decision tree with light gradient boosting.," Measurement: Sensors,, pp. 27, 100726., 2023. |
| [102] | S. Ansari, A. Ayob, M. S. H. Lipu, M. H. Saad and A. Hussain, "A review of monitoring technologies for solar PV systems using data processing modules and transmission protocols: Progress, challenges and prospects," Sustainability, pp. 13(15), 8120., 2021. |
| [103] | Petrosync, "A Complete Guide of Corrosion Monitoring in The Industry,," 1 10 2024. [Online]. Available: https://www.petrosync.com/blog/corrosion-monitoring,. [Accessed 2 3 2025]. |
| [104] | S. Sarkar, K. U. Rao, J. Bhargav, S. Sheshaprasad and A. S. CA, "IoT based wireless sensor network (WSN) for condition monitoring of low power rooftop PV panels," in In 2019 IEEE 4th International Conference on Condition Assessment Techniques in Electrical Systems (CATCON) , 2019. |
| [105] | G. Qiao, G. Sun, Y. Hong, Y. Qiu and J. Ou, " Remote corrosion monitoring of the RC structures using the electrochemical wireless energy-harvesting sensors and networks.," NDT & E International, pp. 44(7), 583-588., 2011. |
| [106] | J. Kampman, J. Masela and T. H. Joubert, "Wireless sensor network for water pipe corrosion monitoring.," in In 2021 IEEE AFRICON, 2021. |
| [107] | P. Pappinisseri Puluckul and M. Weyn, "Battery-less environment sensor using thermoelectric energy harvesting from soil-ambient air temperature differences.," Sensors, pp. 22(13), 4737., 2022. |
| [108] | D. Su, Y. Xia and R. Yuan, "Self‐Powered Wireless Sensor Network for Automated Corrosion Prediction of Steel Reinforcement.," Journal of Sensors, pp. 2018(1), 4125752, 2018. |
| [109] | A. Potnis and C. S. Rajeshwari, "Wireless sensor network: challenges, issues and research.," in In Proceedings of 2015 International Conference on Future Computational Technologies, Singapore, 2015. |
| [110] | F. Wang and J. Liu, "Networked wireless sensor data collection: Issues, challenges, and approaches.," IEEE Communications Surveys & Tutorials,, pp. 13(4), 673-687., 2010. |
| [111] | S. Sharma, R. K. Bansal and S. Bansal, ". (2013, December). Issues and challenges in wireless sensor networks.," in In 2013 international conference on machine intelligence and research advancement, 2013. |
| [112] | G. Sahar, K. A. Bakar, S. Rahim, . N. A. K. Khani, and T. Bibi, "Recent advancement of data-driven models in wireless sensor networks: a survey.," Technologies, pp. 9(4), 76., 2021. |
| [113] | Z. Sheng, C. Mahapatra, C. Zhu and V. C. Leung, "Recent advances in industrial wireless sensor networks toward efficient management in IoT.," IEEE access,, pp. 3, 622-637, 2015. |
| [114] | M. M. Aman, K. H. Solangi, M. S. Hossain, A. Badarudin, G. B. Jasmon, H. Mokhlis and S. N. Kazi, "A review of Safety, Health and Environmental (SHE) issues of solar energy system.," Renewable and Sustainable Energy Reviews, pp. 41, 1190-1204, 2015. |
| [115] | R. Prăvălie, C. Patriche and G. Bandoc, "Spatial assessment of solar energy potential at global scale. A geographical approach.," Journal of Cleaner Production, pp. 209, 692-721, 2019. |
| [116] | K. N. Nwaigwe, P. Mutabilwa and E. Dintwa, "An overview of solar power (PV systems) integration into electricity grids," Materials Science for Energy Technologies,, pp. 2(3), 629-633, 2019. |
| [117] | C. A. Charalambous, A. Demetriou and N. Kokkinos, "Impact of photovoltaic-oriented DC stray current corrosion on large-scale solar farms' grounding and third-party infrastructure: modeling and assessment.," IEEE Transactions on Industry Applications, pp. 51(6), 5421-5430, 2015. |
| [118] | R. R. Hernandez, S. B. Easter, M. L. Murphy-Mariscal, , F. T. Maestre, M. Tavassoli, E. B. Allen and M. F. Allen, "Environmental impacts of utility-scale solar energy.," Renewable and sustainable energy reviews, pp. 29, 766-779, 2014. |
| [119] | M. L. Sousa, S. Dimova, A. Athanasopoulou, G. Rianna, P. Mercogliano, V. Villani and T. Dyngeland, Expected implications of climate change on the corrosion of structures (Doctoral dissertation, Joint Research Centre)., 2020. |
| [120] | J. B. Castro, M. Schweiger, D. Moser, T. Tanahashi, B. H. King, , G. Friesen and J. S. Valencia, "Climatic rating of photovoltaic modules: Different technologies for various operating conditions.," 2020. |
| [121] | R. Brakels, "Solar Panels By The Sea And Corrosion Resistance.," 11 08 2016. [Online]. Available: https://www.solarquotes.com.au/blog/salt-mist. [Accessed 03 03 2025]. |
| [122] | F. A. Canales, P. Sapiega,, E. Kasiulis, E. Jonasson, I. Temiz and J. Jurasz, "Temporal dynamics and extreme events in solar, wind, and wave energy complementarity: Insights from the Polish Exclusive Economic Zone.," Energy,, pp. 305, 132268, 2024. |
| [123] | A. J. Schaffer and S. Brun, "Beyond the sun—Socioeconomic drivers of the adoption of small-scale photovoltaic installations in Germany.," Energy Research & Social Science,, pp. 10, 220-227, 2015. |
| [124] | K. S. Wolske, P. C. Stern and T. Dietz, "Explaining interest in adopting residential solar photovoltaic systems in the United States: Toward an integration of behavioral theories.," Energy research & social science,, pp. 25, 134-151, 2017. |
| [125] | Y. Yue, Z. Yan, P. Ni, F. Lei and G. Qin, " Promoting solar energy utilization: prediction, analysis and evaluation of solar radiation on building surfaces at city scale," Energy and Buildings, pp. 319, 114561, 2024. |
| [126] | A. Moradzadeh, H. Moayyed, B. Mohammadi-Ivatloo, Z. Vale, C. Ramos and R. Ghorbani, "A novel cyber-Resilient solar power forecasting model based on secure federated deep learning and data visualization.," Renewable Energy, pp. 211, 697-705, 2023. |
| [127] | X. Su, Z. Xu, S. Tian, C. Chen, Y. Huang, Y. Geng and J. Chen, "Life cycle assessment of three typical solar energy utilization systems in different regions of China.," Energy, pp. 278, 127736., 2023. |
| [128] | D. G. Labay and T. C. Kinnear, "Exploring the consumer decision process in the adoption of solar energy systems.," Journal of consumer research, pp. 8(3), 271-278, 1981. |
| [129] | M. W. Akram, G. Li, Y. Jin and X. Chen, "Failures of Photovoltaic modules and their Detection: A Review.," Applied Energy, pp. 313, 118822., 2022. |
| [130] | R. Bender, D. Féron, D. Mills, S. Ritter, R. Bäßler, D. Bettge and M. Zheludkevich, "Corrosion challenges towards a sustainable society.," Materials and corrosion,, pp. 73(11), 1730-1751, 2022. |
| [131] | K. A. Weiß, E. KlimM and I. Kaaya, "Accelerated aging tests vs field performance of PV modules," Progress in Energy , pp. 4, 042009., 2022. |
| [132] | F. Sutter, A. Fernández-García, J. Wette, T. J. Reche-Navarro and L. Martínez-Arcos, " Acceptance criteria for accelerated aging testing of silvered-glass mirrors for concentrated solar power technologies," Solar Energy Materials and Solar Cells, pp. 193, 631-371, 2019. |
| [133] | T. C. Diamantino, R. Gonçalves, S. Páscoa, I. N. Alves and M. J. Carvalho, "Accelerated aging tests to selective solar absorber coatings for low temperature applications," Solar Energy Materials and Solar Cells, pp. 232, 111320, 2021. |
| [134] | V. Kumar, "Top 20 Solar Panel Testing Methods: Infinit Lab.," 22 03 2023. [Online]. Available: https://infinitalab.com/blogs/mechanical-properties-of-materials/top-20-solar-panel-testing-methods.. [Accessed 21 02 2025]. |
| [135] | L. Kahana, "New research shows correlation between PV module electrode corrosion and damp heat test: PV focus magazine.," 21 02 2025. [Online]. Available: https://www.pv-magazine.com/2025/02/21/new-research-shows-correlation-between-pv-module-electrode-corrosion-and-damp-heat-test./. [Accessed 03 03 2025]. |
| [136] | H. Park, W. So and W. K. Kim, "Performance evaluation of photovoltaic modules by combined damp heat and temperature cycle test.," Energies,, pp. 14(11), 3328., 2021. |
| [137] | S. H. Kim, H. J. Son, S. H. Park, J. S. Hahn and D. H. Kim, " A study for degradation of flexible organic photovoltaic modules via damp-heat test: By accessing individual layers of the module.," Solar Energy Materials and Solar Cells, pp. 144, 187-, 2016. |
| [138] | D. Wu, J. Zhu, T. R. Betts and R. Gottschalg, "Degradation of interfacial adhesion strength within photovoltaic mini‐modules during damp‐heat exposure. Progress in Photovoltaics:," Research and Applications, pp. 22(7), 796-809, 2014. |
| [139] | M. J. Gunther, "Design and Validation of an Led-Based Solar Simulator for Solar Cell and Thermal Testing (Master's thesis, California Polytechnic State University).," 2020. |
| [140] | S. Brunold, U. Frei, B. Carlsson, K. Möller and M. Köhl, "Accelerated life testing of solar absorber coatings:: Testing procedure and results," Solar Energy, pp. 68(4), 313-323, 2000. |
| [141] | F. Dia, N. Mbengue, O. N. Sarr, M. Diagne, O. A. Niasse, A. Dieye and C. Sene, "Model associated with the study of the degradation based on the accelerated test: A literature review.," Open Journal of Applied Sciences, pp. 6(1), 49-63, 2016. |
| [142] | D. Yang, S. Alessandrini, J. Antonanzas, F. Antonanzas-Torres, V. Badescu, H. G. Beyer and J. Zhang, "Verification of deterministic solar forecasts.," Solar Energy, pp. 210, 20-37, 2020. |
| [143] | W. L. Oberkampf, T. G. Trucano and C. Hirsch, "Verification, validation, and predictive capability in computational engineering and physics.," Appl. Mech. Rev, pp. 57(5), 345-384., 2004. |
| [144] | I. M. T. I. A. Z. SYED IMTIAZ, "VALIDATION STANDARD OPERATING PROCEDURES.," 2021. |
| [145] | B. H. Thacker, S. W. Doebling, F. M. Hemez, M. C. Anderson, J. E. Pepin and E. A. Rodriguez, "Concepts of model verification and validation.," USA, 2004. |
| [146] | H. Böök, A. Poikonen, A. Aarva, T. Mielonen, M. R. Pitkänen and A. V. Lindfors, "Photovoltaic system modeling: a validation study at high latitudes with implementation of a novel DNI quality control method," Solar Energy, pp. 204, 316-329., 2020. |
| [147] | L. Migliorini, L. Molinaroli, R. Simonetti and G. Manzolini, "Development and experimental validation of a comprehensive thermoelectric dynamic model of photovoltaic modules.," Solar Energy, pp. 144, 489-501, 2017. |
| [148] | L. M. Calle, "Corrosion on Mars: Effect of the Mars Environment on Spacecraft Materials (No. NASA/TP-2019-220238).," 2013. |
| [149] | B. Chen, Y. L. Xu and W. L. Qu, "Evaluation of atmospheric corrosion damage to steel space structures in coastal areas.," International Journal of Solids and Structures, pp. 42(16-17), 4673-4694, 2005. |
| [150] | I. M. Alarifi, "Advanced selection materials in solar cell efficiency and their properties-A comprehensive review," in Materials Today: Proceedings 81 , 2023. |
| [151] | Y. Li, "Molecular design of photovoltaic materials for polymer solar cells: toward suitable electronic energy levels and broad absorption.," Accounts of chemical research, pp. 45(5), 723-733, 2012. |
| [152] | S. L. Chawla, "Materials selection for corrosion control," ASM international, 1993. |
| [153] | M. Saifullah, J. Gwak and J. H. Yun, "Comprehensive review on material requirements, present status, and future prospects for building-integrated semitransparent photovoltaics (BISTPV).," Journal of Materials Chemistry A,, pp. 4(22), 8512-8540., 2016. |
| [154] | R. T. Loto and E. Özcan, " Corrosion resistance studies of austenitic stainless steel grades in molten zinc-aluminum alloy galvanizing bath.," Journal of Failure Analysis and Prevention, pp. 16, 427-437, 2016. |
| [155] | M. Ismail, B. Muhammad, E. Hamzah and T. Keong, "Corrosion behaviour of dual‐phase and galvanized steels in concrete," Anti-Corrosion Methods and Materials, pp. 59(3), 132-138., 2012. |
| [156] | P. Shreyas, B. Panda and A. D. Vishwanatha, "Characteristics of stainless steel-galvanized steel joint: Effect of stainless steel composition and welding parameters," in Materials Today: Proceedings,, 2019. |
| [157] | Exactus Energy, " Structural Requirements for Solar Panels - Exactus Energy.," 2024. [Online]. Available: https://www.exactusenergy.com/blog/structural-requirements-for-solar-panels. [Accessed 07 03 2025]. |
| [158] | U. J. Udi, M. M. Yussof, K. M. Ayagi, C. Bedon and M. K. Kamarudin, "Environmental degradation of structural glass systems: A review of experimental research and main influencing parameters," Ain Shams Engineering Journal, pp. 14(5), 101970, 2023. |
| [159] | H. S. Aljibori, A. Alamiery and A. A. H. Kadhum, "Advances in corrosion protection coatings: A comprehensive review.," Int. J. Corros. Scale Inhib, pp. 12(4), 1476-1520, 2023. |
| [160] | h. Fang, Y. Bai, W. Liu, Y. Qi and J. Wang, "Connections and structural applications of fibre reinforced polymer composites for civil infrastructure in aggressive environments.," Composites Part B: Engineering, pp. 164, 129-143, 2019. |
| [161] | Green.org, " Pros and Cons of Hybrid Technology," [Online]. Available: https://green.org/2024/01/30/pros-and-cons-of-hybrid-technology/. [Accessed 06 03 2025]. |
| [162] | S. N. Vodapally and M. H. Ali, "A comprehensive review of solar photovoltaic (PV) technologies, architecture, and its applications to improved efficiency," Energies, pp. 16(1), 319, 2023. |
| [163] | W. P. U. Wijeratne, R. J. Yang, E. Too and R. Wakefield, "Design and development of distributed solar PV systems: Do the current tools work?.," Sustainable cities and society, pp. 45, 553-578, 2019. |
| [164] | G. V. Akimov, "Factors influencing corrosion. Corrosion," pp. 15(9), 23-36., 1959. |
| [165] | Irene Negro, "How PV panel tilt affects solar plant performance: RatedPower a part of Enverus.," 2022. [Online]. Available: https://ratedpower.com/blog/pv-panel-tilt. [Accessed 06 03 2025]. |
| [166] | A. Gomes, M. F. do Nascimento Oliveira and M. Musci, "Optimal Tilt Angle of Photovoltaic Panels: A Case Study in the City of Rio de Janeiro," Environmental Management and Sustainable Development, pp. 12(2), 54-66, 2023. |
| [167] | A. Gedifew and A. Benor, "Evaluating the impact of tilt angles and tracking mechanisms on photovoltaic modules in Ethiopia," Frontiers in Energy Research, pp. 12, 1519725, 2025. |
| [168] | M. L. Adekanbi, E. S. Alaba, T. J. John, T. D. Tundealao and T. I. Banji, "Soiling loss in solar systems: A review of its effect on solar energy efficiency and mitigation techniques.," Cleaner Energy Systems, pp. 7, 100094., 2024. |
| [169] | K. Adolf and A. Uzorka, "Effects of substrates on the efficiency of a monocrystalline solar panel," Scientific Reports, pp. 15(1), 6667, 2025. |
| [170] | A. Goswami, P. Sadhu, U. Goswami and P. K. Sadhu, "Floating solar power plant for sustainable development: A techno‐economic analysis.," Environmental Progress & Sustainable Energy, pp. 38(6), e13268, 2019. |
| [171] | K. Mohan, "Microbial deterioration and degradation of polymeric materials.," Journal of Biochemical Technology,, pp. 2(4), 210-215, 2011. |
| [172] | M. J. Alshareef, "A comprehensive review of the soiling effects on PV module performance.," IEEE Access, pp. 11, 134623-134651, 2023. |
| [173] | A. M. Aly, "Breaking boundaries in wind engineering: LSU WISE open-jet facility revolutionizes solar panel and building design.," Applied Sciences, pp. 13(23), 12546, 2023. |
| [174] | V. V. Pillai, B. Ramasubramanian, O. Sequerth, S. Pilla, T. Wang, A. K. Mohanty and N. Hameed , "Nanomaterial advanced smart coatings: Emerging trends shaping the future," Applied Materials Today, pp. 42, 102574, 2025. |
| [175] | Y. Li, J. Wang, S. Li, Y. Wu, J. Wang, F. Cao and G. Qin, " Solar energy protects steels against corrosion: Enhanced protection capability achieved by NiFeOx decorated BiVO4 photoanode," Materials Research Bulletin, pp. 107, 416-420., 2018. |
| [176] | R. Claus and M. López, "Key issues in the design of floating photovoltaic structures for the marine environment," Renewable and Sustainable Energy Reviews , pp. 164, 112502., 2022. |
| [177] | Guadian Glass, Guardian GlassTime Technical Manual, Mexico: Guardian Europe S.à r.l., 2022. |
| [178] | H. W. Cui, D. S. Li, Q. Fan and H. X. Lai, "Electrical and mechanical properties of electrically conductive adhesives from epoxy, micro-silver flakes, and nano-hexagonal boron nitride particles after humid and thermal aging," International Journal of Adhesion and Adhesives, pp. 44, 232-236., 2013. |
| [179] | V. Vasagar, M. K. Hassan, , A. M. Abdullah, A. V. Karre, B. Chen, K. Kim and T. Cai, "Non-destructive techniques for corrosion detection: A review," Corrosion Engineering, Science and Technology, pp. 59(1), 56-85, 2024. |
| [180] | J. Y. Hu, S. S. Zhang, E. Chen and W. G. Li, "A review on corrosion detection and protection of existing reinforced concrete (RC) structures.," Construction and Building Materials, pp. 325, 126718, 2022. |

[181]  S. Dolui, B. Sahu, D. Kumar and S. Banerjee, "Facile access to redox responsive self-healing coating   materials via living cationic block copolymerization of styrene and 2-chloroethyl vinyl ether," European Polymer Journal, , pp. 196, 112251., 2023.

[182] Atta, Solomon, Mairura Lydiah Kerubo, Nyaera Emily Sabisa, Daniel Adu-Gyamfi, Stephen A. Appiah, and Emeka E. Onyishi. 2025. “Environmental Corrosion and Long-Term Degradation of Crystalline Silicon Solar Cells: Mechanisms, Climate Effects and Mitigation Strategies”. Current Journal of Applied Science and Technology 44 (10):9-18. https://doi.org/10.9734/cjast/2025/v44i104616.

[183] Z. Rana et al., “Solar panel corrosion: a review,” International Journal of Molecular Sciences, vol. 26, no. 13, p. 5960, Jun. 2025, doi: 10.3390/ijms26135960.

[184] A. Radhakrishnan, M. Tharmaraj, and N. Srinivasan, “A photocathodic corrosion protection performance of aluminium frames in solar panels using TiO2/C3N4 heterostructure,” Journal of Alloys and Compounds, vol. 1028, p. 180707, May 2025, doi: 10.1016/j.jallcom.2025.180707.