Original Research Article

POWER LOSS MITIGATION USING DISTRIBUTED GENERATTION IN ASABA DISTRIBUTION NETWORK.

ABSTRACT

The increasing demand for electricity, coupled with rising economic and environmental concerns, has made renewable energy, particularly solar energy, a major area of interest. This research work evaluates the impact of distributed generation (DG) and presents a methodology for the optimal allocation and sizing of distributed generation within a distribution network in order to minimise power losses and improve voltage profiles. The study involved load flow analysis of the existing 15MVA, 33/11kV Benin Electricity Distribution Company (BEDC) Asaba injection substation distribution network and its 11kV radial feeders (SPC and Anwai Road), connected to an aggregate of ninety-six (96) 11/0.415kV secondary distribution transformers serving as load buses. Simulation, analysis, and integration of photovoltaic (PV) distributed generation into the Asaba injection substation distribution network were carried out using the Newton–Raphson algorithm and the Loss Sensitivity Factor (LSF) algorithm to determine the optimal location and size of the DG units. The network was modelled in ETAP version 12.6 using a detailed single-line diagram developed in the ETAP editing environment. The results revealed that, prior to DG installation, only ten (10) out of the ninety-six (96) buses operated within the statutory voltage limits of 394.25V–435.75V (0.95–1.05 p.u.), while eighty-six (86) buses violated the permissible voltage range. This indicated that the network was weak, unstable, and characterised by high active and reactive power losses of 1329.08kW and 2031.16kVAr, respectively. Following the optimal placement of DG units, active and reactive power losses were reduced by 57.5% and 70.7%, respectively. In addition, ninety-one (91) out of the ninety-six (96) buses operated within the statutory voltage limits. This improvement significantly enhanced the capacity, reliability, and operational efficiency of the distribution network.

Keywords: Distributed generation, optimal sizing, Loss Sensitivity Factor, optimal location, injection substation, distribution network, ETAP, Newton–Raphson, photovoltaic.

1. INTRODUCTION

Electricity, one of the most versatile forms of energy, plays a critical role in the socio-economic and technological development of every nation. Global demand for electrical energy continues to increase due to population growth, expanding economic activities, social advancement, and rapid industrialisation [1]. The availability, reliability, affordability, and sustainability of electricity are among the key indicators used to assess a nation’s industrial development, as modern industries depend on affordable, sustainable, and uninterrupted power supply. Nations experiencing inadequate electricity supply often face economic stagnation and reduced investor confidence [2].

Nigeria continues to face significant electricity challenges despite its abundant natural resources, as energy demand considerably exceeds supply. There is a strong relationship between socio-economic development and access to reliable electricity. Nigeria’s power sector operated as a government monopoly for several decades until reforms were introduced in 2005 through the Electric Power Sector Reform Act [3]. Under this arrangement, only the Federal Government was authorised to own electricity generation, transmission, and distribution infrastructure. This centralised structure limited the expansion and improvement of electricity services despite increasing economic activities and population growth.

Currently, Nigeria generates approximately 4,000 MW of electricity for a population exceeding 200 million people, creating one of the widest electricity demand-supply gaps in the world [4]. In comparison, South Africa generates over 40,000 MW, while Brazil generates above 100,000 MW [5]. The unreliable nature of electricity supply, depletion of fossil fuel resources, and instability in the power sector have forced many consumers to depend on petrol and gas-powered generators. This has contributed to fuel scarcity and environmental pollution [6].

Despite the energy deficit, renewable energy resources such as Solar Energy, Wind Energy, biomass, hydrogen, and fuel cells remain largely underutilised in Nigeria. The energy shortage has significantly affected industrial productivity across the country. To meet increasing electricity demand and minimise technical losses, distributed generation based on renewable energy technologies has emerged as a viable alternative to conventional energy sources. When optimally integrated into distribution networks, DG systems can significantly improve voltage profiles, reduce power losses, enhance reliability, increase system efficiency, and reduce greenhouse gas emissions [7], [8].

Compared with other loss reduction techniques such as optimal capacitor placement and network reconfiguration, distributed generation has proven more effective. While capacitor placement primarily affects reactive power flow, DG units influence both active and reactive power flows within the distribution network [9]. The continuous growth in DG adoption can be attributed to environmental concerns, technical advantages, and reduced capital investment requirements. However, improper placement and sizing of DG units may lead to adverse effects such as voltage instability, network congestion, unwanted islanding, harmonics, and voltage fluctuations [10].

This research investigates the impact of distributed generation on the 33/11 kV, 2 × 15 MVA Asaba injection substation operated by Benin Electricity Distribution Company. The study identifies buses experiencing voltage violations, evaluates the extent of these violations, and determines the network’s load-carrying capacity. Furthermore, a photovoltaic distributed generation system was integrated into the network to improve load capacity, determine its optimal size and location, mitigate voltage violations, and minimise technical power losses.

2. LITERATURE REVIEW ON DISTRIBUTED GENERATION

The planning and integration of distributed generation as shown in Figure 1 have received considerable attention in recent years due to the need to maximise the benefits of modern power generation technologies. Researchers have proposed various methods for reducing power losses in distribution systems through optimal DG allocation. Proper placement and sizing of DG units play a significant role in loss minimisation [11]. Several analytical methods have been proposed to determine the optimal location of DG units in radial distribution systems for loss reduction under unity power factor conditions. However, some of these studies did not consider the optimal sizing of DG units. Other researchers developed faster analytical approaches based on current injection matrices, eliminating the need for impedance or inverse admittance matrices in determining optimal DG placement [12].

An exact loss formula-based analytical method has also been proposed to determine both the optimal size and location of DG units in primary distribution systems for power loss minimisation [13]. Further studies introduced analytical expressions for determining the optimal power factor and sizing of different DG types. These methods were validated on various distribution test systems and later improved to enhance computational efficiency [14]. Probabilistic approaches such as Mixed Integer Nonlinear Programming (MINLP) have also been used to minimise annual energy losses. In these studies, renewable DG technologies such as solar, biomass, and wind were evaluated for their effectiveness in reducing losses [15].

Although many studies considered DG units supplying only active power, better system performance can be achieved when DG units supply both active and reactive power. Due to the high computational burden associated with many analytical techniques, researchers have increasingly focused on heuristic and artificial intelligence-based optimisation methods such as Fuzzy Genetic Algorithms, curve-fitting heuristic techniques, and Particle Swarm Optimisation for DG placement and sizing [16]

3. METHODOLOGY

This study investigates the impact of distributed generation on improving load ability, mitigating voltage violations, and minimising power losses within the 11kV distribution network of the BEDC Asaba 2 × 15MVA, 33/11kV injection substation located in Asaba. The injection substation has four outgoing 11kV feeders, namely:

- SPC Feeder.

- Anwai Road Feeder.

- Commercial Feeder.

- Express Road Feeder.

Only one 15MVA power transformer (T1) and its associated bus coupler in normally open position were considered in this study. From transformer T1, two feeders—SPC and Anwai Road feeders—were selected for analysis, while transformer T2 and its associated feeders were excluded. The selected distribution network consists of ninety-six (96) secondary distribution transformers: SPC Feeder (45 transformers) and Anwai Road Feeder (51 transformers). The data for the study were obtained from BEDC Asaba during peak load conditions and methodologies adopted include:

- Determination of feeder parameters.

- Collection of transformer ratings and line conductor specifications.

- Measurement of route lengths.

- Peak load assessment of buses.

- Determination of phase voltages, power factors, and active power demand.

- Development of a detailed single-line diagram in ETAP 12.6 as shown in Figure 3.

Load flow simulation was performed using the Newton–Raphson algorithm in ETAP 12.6. The Loss Sensitivity Factor algorithm was then applied to determine the optimal location and size of the photovoltaic DG system. The performance of the improved network was subsequently compared with that of the original network.

4. OPTIMAL LOCATION, SIZING, AND PLACEMENT OF DG

To mitigate system losses identified from the initial load flow analysis, network compensation was required. The Loss Sensitivity Factor (LSF) method was employed to identify candidate buses where DG placement would achieve maximum loss reduction and network performance improvement. This approach reduces the search space and facilitates efficient identification of optimal DG placement locations within the network using the flow chart as shown in Figure 2. The mathematical formulation of active power loss and DG sizing used in this work follows the analytical models developed by Nara Acharya et al [11] and further improved by D. Q. Hung et al. [14], [17].

The active power loss in the distribution network can be determined using Equation (1).

Plinelosq= [Peffq2+Qeffq2]RkVq2					(1)

Where  Qeff (q) and  Peff (q)  are the effective reactive and active power flows supplied beyond the node ‘q’

∂Plinelosq∂ Peff (q)=2*Peff (q)*RkVq2						(2)

∂Plinelosq∂ Qeff (q)=2*Qeff (q)*RkVq2						(3)

Equation (2) and (3) help in calculating the sensitivity factors of the buses and they are ranked in value. The buses having high value of LSF is considered as highest priority one. It is necessary to consider LSF based on both proximity and priority of buses towards load and generation. This is due to the fact that if we consider LSF based on priority list alone, it may indicate nearby buses as optimal site for placing DGs which makes the identified sites ineffective to satisfy the objectives [14]. The actual loss formula used in determining the active power loss of the system can be obtained from the active power injected based on loss sensitivity factor:

PL=i=1Ni=jNαijPiPj+QiQj+βijQiPj-PiQj			(4)

Where,

αij=rijViVjcosδi-δj; βij=rijViVjsinδi-δj			(5)

Based on the active power injected on the i th bus, the loss sensitivity factor of the particular bus can be represented as:

αij=∂PL∂Pi=2j=1N(αijPj-βijQj)=2QRV2				(6)

The active and reactive power injected at bus i, where the DG located, are given by (7) and (8), respectively [12, 15]

Pi=PDGi-PDi							(7)

Qi=QDGi-QDi=Pi=aPDGi-QDi				(8)

From (4), (7), and (8), the active power loss can be rewritten as

PL=i=1Nj=1NαijPDGi-PDiPj+aPDGi-QDiQj+βijaPDGi-PDiPj-PDGi-PDiQj							(9)

If the partial derivative of equation (9) with respect to the active power injection from DG at bus i becomes zero then, the total active power loss of the system is minimum. By simplification and rearrangement, equation (9) becomes;

αiiPi+aQi+βiiaPi-Qi+j=1j≠1NαijPj-βijQj+aj=1j≠1NαijQj+βijPj=0(10)

Let, Xi=j=1j≠1NαijPj-βijQj, Yi= j=1j≠1NαijQj+βijPj		 (11)

From equations 7,8,10 and 11, equation (12) was developed;

αiiPDGi-PDi+a2PDGi-aQDi+βiiQDi-aPDi+Xi+aYi=0	(12)

Hence, the optimal size of DG at each bus i for minimizing loss can be written as;

PDGi=αiiPDi+aQDi+βiiaPDi-QDi-Xi-aYia2αii+αii	(13)

Figure 1: A typical layout of Distributed Generation

Start

Enter the number of DG units

Run load flow for the base case and calculate losses

Find the DG optimal location base on LSF

Update load data to allocated next DG

One of the constraints is unsatisfied?

Stop and print the results

End

Yes

No

Find the DG optimal size with the minimum loss at the optimal location by running load flow

Figure 2: Flow chart of optimal location and sizing base on LSF

Table 1: Load Flow Result Showing Active and Reactive Power Flow and Losses with and without DG placement.

|  |  |  | WITH DG PLACEMENT |  |  |  |  | WITHOUT DG PLACEMENT |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| S/N | From Bus | To Bus | kW Flow | kvar Flow | Amp Flow | kW Losses | kvar Losses | kW Flow | kvar Flow | Amp Flow | kW Losses | kvar Losses |
| 1 | ABBEY S/S | ABBEY | 6.23 | 2.06 | 0.345 | 0.0096 | 0.0143 | 5.08 | 1.68 | 0.311 | 0.008 | 0.0117 |
| 2 | ABUTA S/S | ABUTA | 280.2 | 99.94 | 15.8 | 6.71 | 10.06 | 218.8 | 78.07 | 13.97 | 5.24 | 7.86 |
| 3 | AIRTEL S/S | AIRTEL | 57.54 | 19.88 | 3.206 | 0.828 | 1.24 | 46.56 | 16.09 | 2.884 | 0.67 | 1 |
| 4 | AIRTELS S/S | AIRTELS | 81.18 | 28.66 | 4.575 | 1.69 | 2.53 | 72.05 | 25.43 | 4.31 | 1.5 | 2.24 |
| 5 | ALUME DRIVE S/S | ALUME DRIVE | 229.2 | 80.53 | 12.83 | 4.42 | 6.63 | 199.5 | 70.08 | 11.97 | 3.85 | 5.77 |
| 6 | ANWAI CAMPUS S/S | ANWAI CAMPUS | 378.5 | 133.4 | 21.81 | 7.67 | 11.5 | 335.9 | 118.4 | 20.55 | 6.8 | 10.2 |
| 7 | ANWAI GRA II S/S | ANWAI GRA II | 225.8 | 79.47 | 12.95 | 4.5 | 6.75 | 200.4 | 70.53 | 12.2 | 3.99 | 5.99 |
| 8 | ANWAI I S/S | ANWAI I | 206.5 | 72.05 | 11.54 | 3.57 | 5.36 | 188.1 | 65.63 | 11.01 | 3.26 | 4.88 |
| 9 | ANWAI II S/S | ANWAI II | 313.3 | 108.7 | 17.41 | 4.88 | 7.32 | 281.2 | 97.56 | 16.49 | 4.38 | 6.57 |
| 10 | ANWAI RIVER S/S | ANWAI RIVER | 254.1 | 90.21 | 14.61 | 5.73 | 8.59 | 225.5 | 80.06 | 13.76 | 5.08 | 7.62 |
| 11 | ARCH. MARTINS ODIAKA S/S | ARCH. MARTINS ODIAKA | 97.72 | 34.97 | 5.493 | 2.43 | 3.65 | 92.66 | 33.16 | 5.349 | 2.3 | 3.46 |
| 12 | BAKARE S/S | BAKARE | 221.1 | 77.56 | 12.48 | 4.18 | 6.27 | 172.2 | 60.4 | 11.01 | 3.25 | 4.88 |
| 13 | BENCLINTON S/S | BENCLINTON | 109.9 | 37.91 | 6.167 | 1.53 | 2.3 | 87.09 | 30.05 | 5.49 | 1.21 | 1.82 |
| 14 | BENITA I S/S | BENITA I | 224.6 | 78.83 | 12.61 | 4.27 | 6.4 | 179.8 | 63.11 | 11.28 | 3.42 | 5.12 |
| 15 | BENITA II S/S | BENITA II | 243 | 85.74 | 13.65 | 5 | 7.5 | 194.6 | 68.64 | 12.21 | 4.01 | 6.01 |
| 16 | BISHOP CHUKWUMA S/S | BISHOP CHUKWUMA | 369.5 | 129.5 | 20.73 | 6.92 | 10.38 | 323.8 | 113.5 | 19.41 | 6.07 | 9.1 |
| 17 | BUDGET S/S | BUDGET | 358.1 | 125.2 | 19.91 | 6.39 | 9.58 | 292 | 102.1 | 17.98 | 5.21 | 7.81 |
| 18 | Bus4 | GOVERNMENT CORE ASABA | 610.8 | 763 | 51.66 | 0.202 | 0.1 | 8212 | 2872.9 | 470.4 | 16.76 | 8.3 |
| 19 | Bus6 | Bus4 | 610.6 | 762.9 | 51.66 | 0.404 | 0.2 | 8195.3 | 2864.6 | 470.4 | 33.52 | 16.59 |
| 20 | ECOBANK S/S | Bus6 | 610.2 | 762.7 | 51.66 | 0.404 | 0.2 | 8161.8 | 2848 | 470.4 | 33.52 | 16.59 |
| 21 | Bus9 | ECOBANK S/S | 587.9 | 755.3 | 50.64 | 0.777 | 0.385 | 8107.7 | 2824.6 | 469.2 | 66.7 | 33.02 |
| 22 | Bus10 | Bus9 | 326.4 | 115.2 | 18.33 | 0.158 | 0.0524 | 301.2 | 106.4 | 17.61 | 0.146 | 0.0484 |
| 23 | JOBAS S/S | Bus10 | 254.9 | 90.22 | 14.32 | 0.0193 | 0.0064 | 235.2 | 83.27 | 13.76 | 0.018 | 0.0059 |
| 24 | WATER BOARD S/S | Bus9 | 260.8 | 639.6 | 36.58 | 0.0403 | 0.0243 | 7739.8 | 2685.2 | 451.6 | 6.15 | 3.7 |
| 25 | Bus18 | WATER BOARD S/S | 259.5 | 639.2 | 36.53 | 0.282 | 0.17 | 7732.5 | 2681.2 | 451.5 | 43.03 | 25.9 |
| 26 | SPC S/S | Bus18 | 148.2 | 600.7 | 32.78 | 0.0407 | 0.0201 | 7588.3 | 2620.3 | 445.6 | 7.52 | 3.72 |
| 27 | FMC S/S | SPC S/S | 232 | -467.1 | 27.63 | 0.202 | 0.1 | 7235.3 | 2495.3 | 425.2 | 47.94 | 23.73 |
| 28 | Bus24 | FMC S/S | 594 | -340.5 | 36.25 | 0.625 | 0.0922 | 6863.3 | 2358 | 406 | 78.46 | 11.57 |
| 29 | BISHOP CHUKWUMA S/S | Bus24 | 369.5 | 129.6 | 20.73 | 0.0404 | 0.0134 | 323.8 | 113.5 | 19.41 | 0.035 | 0.0117 |
| 30 | Bus30 | Bus24 | 963.6 | -210.9 | 52.22 | 0.103 | 0.0511 | 6461 | 2232.9 | 386.6 | 5.66 | 2.8 |
| 31 | MTN II S/S | Bus30 | 57.53 | 19.89 | 3.222 | 0.0027 | 0.0007 | 50.32 | 17.39 | 3.014 | 0.002 | 0.0006 |
| 32 | Bus33 | Bus30 | 1022 | -190.9 | 54.99 | 0.355 | 0.0676 | 6405.1 | 2212.7 | 383.6 | 17.29 | 3.29 |
| 33 | HELIUS TOWER S/S | Bus33 | 68.04 | 23.74 | 3.814 | 0.0023 | 0.0003 | 59.16 | 20.64 | 3.556 | 0.002 | 0.0003 |
| 34 | Bus38 | Bus33 | 1090 | -167.1 | 58.33 | 0.24 | 0.0456 | 6328.6 | 2188.8 | 380 | 10.18 | 1.94 |
| 35 | Bus43 | Bus38 | 1211 | -125.2 | 64.39 | 0.487 | 0.0927 | 6213.9 | 2150.6 | 373.7 | 16.41 | 3.12 |
| 36 | Bus51 | Bus43 | 1499 | -22.57 | 79.23 | 0.738 | 0.14 | 5950.2 | 2059.2 | 358.8 | 15.12 | 2.88 |
| 37 | ONOCHIE S/S | Bus43 | 287 | 102.5 | 16.12 | 0.0548 | 0.0139 | 247.3 | 88.3 | 14.96 | 0.047 | 0.012 |
| 38 | Bus38 | USONIA HOUSE S/S | 120.7 | 41.82 | 6.757 | 0.0027 | 0.0009 | 104.6 | 36.23 | 6.29 | 0.002 | 0.0008 |
| 39 | Bus53 | Bus51 | 1707 | 49.98 | 90.19 | 1.91 | 0.364 | 5758 | 1994.5 | 348.1 | 28.47 | 5.42 |
| 40 | Bus51 | OKELUE S/S | 206.8 | 72.18 | 11.58 | 0.0079 | 0.0026 | 177.1 | 61.82 | 10.71 | 0.007 | 0.0022 |
| 41 | Bus53 | ODIACHI I S/S | 691.9 | 240.8 | 38.68 | 0.545 | 0.181 | 585.7 | 203.9 | 35.59 | 0.461 | 0.153 |
| 42 | ODIACHI I S/S | NDDC S/S | 236.5 | 83.26 | 13.25 | 0.0516 | 0.0171 | 200.2 | 70.48 | 12.19 | 0.044 | 0.0145 |
| 43 | ODIACHI II S/S | ODIACHI I S/S | 221.2 | 77.53 | 12.39 | 0.036 | 0.012 | 187.2 | 65.63 | 11.4 | 0.031 | 0.0101 |
| 44 | MTN III S/S | ODIACHI I S/S | 6.13 | 2.04 | 0.341 | 0 | 0 | 5.19 | 1.72 | 0.314 | 0 | 0 |
| 45 | Bus68 | Bus53 | 2404 | 291.7 | 127.6 | 4.59 | 0.874 | 5143.9 | 1785.3 | 312.5 | 27.53 | 5.24 |
| 46 | Bus69 | Bus68 | 611.7 | 219.5 | 34.25 | 0.857 | 0.217 | 510.6 | 183.2 | 31.29 | 0.715 | 0.181 |
| 47 | UMUAGU II S/S | Bus69 | 330.1 | 119.3 | 18.52 | 0.039 | 0.0099 | 275.5 | 99.57 | 16.92 | 0.033 | 0.0082 |
| 48 | BUDGET S/S | Bus68 | 3028 | 513.5 | 161.2 | 12.21 | 2.32 | 4605.8 | 1596.8 | 281.2 | 37.16 | 7.07 |
| 49 | STARCOM S/S | ABBEY S/S | 2618 | 956.6 | 146.3 | 0.503 | 0.0957 | 4270.4 | 1485.7 | 262.9 | 1.62 | 0.309 |
| 50 | ABBEY S/S | BUDGET S/S | 2624 | 958.7 | 146.6 | 0.354 | 0.0673 | 4276.6 | 1487.6 | 263.2 | 1.14 | 0.217 |
| 51 | FUNNAYA S/S | OKECHUKWU OKAFOR S/S | 72.58 | 25.39 | 4.039 | 0.0026 | 0.0007 | 59.11 | 20.68 | 3.645 | 0.002 | 0.0005 |
| 52 | Bus87 | FUNNAYA S/S | 334.2 | 118 | 18.61 | 0.106 | 0.0351 | 272.2 | 96.14 | 16.79 | 0.086 | 0.0286 |
| 53 | Bus104 | Bus87 | 2278 | 836.7 | 127.4 | 6.87 | 1.31 | 3991 | 1387.6 | 245.9 | 25.57 | 4.86 |
| 54 | AIRTEL S/S | Bus104 | 57.54 | 19.88 | 3.206 | 0.0016 | 0.0002 | 46.56 | 16.09 | 2.884 | 0.001 | 0.0002 |
| 55 | Bus112 | Bus104 | 2213 | 815.5 | 124.2 | 10.51 | 2 | 3918.8 | 1366.7 | 243 | 40.23 | 7.65 |
| 56 | STADIUM OFFICE S/S | BENITA I S/S | 468.1 | 164.7 | 26.26 | 0.425 | 0.108 | 374.8 | 131.8 | 23.5 | 0.341 | 0.0862 |
| 57 | Bus112 | STADIUM OFFICE S/S | 766.9 | 271.7 | 43.04 | 0.241 | 0.0609 | 614 | 217.5 | 38.51 | 0.193 | 0.0488 |
| 58 | BENITA I S/S | BENITA II S/S | 243.1 | 85.75 | 13.65 | 0.0545 | 0.0138 | 194.6 | 68.65 | 12.21 | 0.044 | 0.011 |
| 59 | Bus121 | Bus112 | 1436 | 541.7 | 81.18 | 4.18 | 0.795 | 3264.6 | 1141.5 | 204.5 | 26.52 | 5.05 |
| 60 | Bus121 | Bus122 | 451.1 | 156.8 | 25.33 | 0.098 | 0.0325 | 357.6 | 124.3 | 22.55 | 0.078 | 0.0258 |
| 61 | Bus122 | Bus125 | 341.1 | 118.8 | 19.17 | 0.0647 | 0.0215 | 270.4 | 94.19 | 17.06 | 0.051 | 0.017 |
| 62 | Bus125 | MTN IV S/S | 6.08 | 2.02 | 0.34 | 0 | 0 | 4.82 | 1.6 | 0.303 | 0 | 0 |
| 63 | Bus125 | PARKISON S/S | 335 | 116.8 | 18.83 | 0.0749 | 0.0249 | 265.5 | 92.57 | 16.76 | 0.059 | 0.0197 |
| 64 | STADIUM S/S | Bus121 | 980.5 | 384.2 | 55.86 | 0.293 | 0.0558 | 2880.5 | 1012.2 | 181.9 | 3.11 | 0.592 |
| 65 | ICON S/S | STADIUM S/S | 552.7 | 232.7 | 31.82 | 0.595 | 0.113 | 2539.1 | 891.7 | 160.5 | 15.13 | 2.88 |
| 66 | Bus151 | Bus150 | 17.09 | -29.28 | 1.801 | 0.0006 | 0.0001 | 2073.5 | 728.8 | 132.1 | 3.28 | 0.624 |
| 67 | Bus150 | ABUTA S/S | 280.2 | 99.96 | 15.8 | 0.0587 | 0.0195 | 218.9 | 78.08 | 13.97 | 0.046 | 0.0152 |
| 68 | Bus150 | ICON S/S | 263.2 | 129.3 | 15.57 | 0.057 | 0.0108 | 2297.4 | 807.9 | 146.1 | 5.01 | 0.954 |
| 69 | Bus160 | Bus151 | 1859 | 614.7 | 103.6 | 6.82 | 1.01 | 641.4 | 227.5 | 40.97 | 1.07 | 0.157 |
| 70 | Bus160 | MTN V S/S | 6.11 | 2.03 | 0.341 | 0 | 0 | 4.71 | 1.56 | 0.299 | 0 | 0 |
| 71 | Bus160 | ENGR. ENENMOH S/S | 67.82 | 22.97 | 3.79 | 0.0029 | 0.001 | 52.28 | 17.71 | 3.328 | 0.002 | 0.0007 |
| 72 | Bus160 | INALU II S/S | 1936 | 640.2 | 107.8 | 3.32 | 0.489 | 583.3 | 208.1 | 37.34 | 0.398 | 0.0587 |
| 73 | INALU II S/S | INALU I S/S | 2210 | 734 | 122.2 | 16.12 | 2.38 | 384.7 | 137.8 | 24.65 | 0.656 | 0.0967 |
| 74 | Bus151 | Bus172 | 1835 | 643 | 103.3 | 4.74 | 0.699 | 1428.9 | 500.7 | 91.14 | 3.69 | 0.544 |
| 75 | Bus152 | Bus172 | 1609 | 564.7 | 90.8 | 0.969 | 0.184 | 1253 | 439.7 | 80.13 | 0.754 | 0.144 |
| 76 | IBUSA RD I S/S | Bus152 | 1355 | 474.9 | 76.5 | 4.4 | 0.837 | 1055.2 | 369.8 | 67.51 | 3.43 | 0.652 |
| 77 | IBUSA RD I S/S | OGBEAMAI S/S | 384 | 135.1 | 21.75 | 0.0834 | 0.0277 | 299 | 105.2 | 19.2 | 0.065 | 0.0216 |
| 78 | ST. JOSEPH S/S | Bus195 | 252.9 | 89.57 | 14.3 | 0.0096 | 0.0032 | 197 | 69.75 | 12.62 | 0.008 | 0.0025 |
| 79 | MTV VI S/S | IBUSA RD I S/S | 611.6 | 214.6 | 34.64 | 0.0705 | 0.0234 | 476.2 | 167.1 | 30.57 | 0.055 | 0.0182 |
| 80 | OGBEKE SQ. S/S | MTV VI S/S | 610.3 | 214.6 | 34.58 | 0.562 | 0.107 | 475.3 | 167.1 | 30.51 | 0.438 | 0.0832 |
| 81 | ONAJEI S/S | OGBEKE SQ. S/S | 225.4 | 79.2 | 12.78 | 0.115 | 0.0219 | 175.5 | 61.67 | 11.28 | 0.09 | 0.0171 |
| 82 | Bus152 | Bus195 | 253 | 89.58 | 14.3 | 0.0673 | 0.0128 | 197 | 69.76 | 12.62 | 0.052 | 0.01 |
| 83 | Bus199 | Bus198 | 257.1 | 924.4 | 50.72 | 0.39 | 0.193 | 8213.9 | 2858.2 | 470.2 | 33.49 | 16.58 |
| 84 | Bus199 | FAVORITE S/S | 621.2 | 217.5 | 34.8 | 0.114 | 0.0378 | 589 | 206.2 | 33.88 | 0.108 | 0.0358 |
| 85 | FAVORITE S/S | NWOBOSHI S/S | 529.3 | 186 | 29.67 | 0.465 | 0.154 | 501.9 | 176.4 | 28.89 | 0.441 | 0.146 |
| 86 | NWOBOSHI S/S | ARCH. MARTINS ODIAKA S/S | 322.6 | 113.9 | 18.11 | 0.0116 | 0.0038 | 305.9 | 108 | 17.63 | 0.011 | 0.0036 |
| 87 | ARCH. MARTINS ODIAKA S/S | DAVNOTCH S/S | 224.8 | 78.9 | 12.61 | 0.0617 | 0.0205 | 213.2 | 74.82 | 12.28 | 0.059 | 0.0194 |
| 88 | FIRS S/S | Bus199 | 364.9 | -706.7 | 42.04 | 0.43 | 0.109 | 7591.4 | 2635.4 | 436.3 | 46.36 | 11.74 |
| 89 | TOBI I S/S | FIRS S/S | 371.4 | -704.5 | 42.1 | 0.432 | 0.109 | 7539.3 | 2621.8 | 436 | 46.29 | 11.72 |
| 90 | Bus213 | TOBI I S/S | 606 | -622 | 45.89 | 0.342 | 0.0866 | 7276.2 | 2533.8 | 423.3 | 29.1 | 7.37 |
| 91 | CHYKES S/S | Bus213 | 276.9 | -358.3 | 23.93 | 0.232 | 0.0588 | 5701.6 | 1989.5 | 333.1 | 45.04 | 11.4 |
| 92 | ANWAI I S/S | Bus213 | 906.9 | -63.73 | 47.97 | 1.49 | 0.378 | 1016.8 | 353.8 | 59.39 | 2.29 | 0.58 |
| 93 | Bus1 | TOBI II S/S | 289.8 | 101.4 | 16.18 | 0.085 | 0.0215 | 263 | 92.03 | 15.41 | 0.077 | 0.0195 |
| 94 | TOBI II S/S | SKY LYN HOTEL S/S | 68.55 | 23.91 | 3.828 | 0.0048 | 0.0012 | 62.2 | 21.7 | 3.646 | 0.004 | 0.0011 |
| 95 | MTN ANWAI RD S/S | Bus1 | 1405 | 110.2 | 74.24 | 0.895 | 0.227 | 562.8 | 195.4 | 32.96 | 0.176 | 0.0447 |
| 96 | MTN ANWAI RD S/S | DESIRE&LESURE GARDEN S/S | 1466 | 131 | 77.45 | 1.07 | 0.271 | 508.9 | 176.8 | 29.82 | 0.159 | 0.0402 |
| 97 | DESIRE&LESURE GARDEN S/S | ZANZIBAR S/S | 1623 | 185.9 | 85.81 | 2.99 | 0.757 | 369.4 | 127.8 | 21.64 | 0.19 | 0.0481 |
| 98 | ZANZIBAR S/S | ANWAI II S/S | 1722 | 219.9 | 91.12 | 1.62 | 0.409 | 281.3 | 97.57 | 16.49 | 0.053 | 0.0134 |
| 99 | CHINEDU OKO S/S | Bus213 | 576 | 199.5 | 32.21 | 0.0842 | 0.0213 | 528.7 | 183.1 | 30.86 | 0.077 | 0.0196 |
| 100 | TEMPO CLINIC I S/S | CHINEDU OKO S/S | 446.1 | 154.3 | 24.95 | 0.202 | 0.0512 | 409.5 | 141.7 | 23.9 | 0.186 | 0.047 |
| 101 | TEMPO CLINIC II S/S | TEMPO CLINIC I S/S | 216.5 | 75.79 | 12.13 | 0.0549 | 0.0139 | 198.7 | 69.56 | 11.62 | 0.05 | 0.0128 |
| 102 | Bus237 | CHYKES S/S | 550.9 | -260.9 | 32.19 | 0.471 | 0.119 | 5409.4 | 1890.1 | 318.5 | 46.12 | 11.68 |
| 103 | Bus237 | UDUAGHAN II S/S | 3910 | 911.2 | 211.6 | 7.27 | 1.84 | 2388.4 | 839.9 | 141.9 | 3.27 | 0.828 |
| 104 | UDUAGHAN II S/S | HILIOUS TOWER S/S | 81.37 | 28.69 | 4.547 | 0.0067 | 0.0017 | 71.75 | 25.3 | 4.27 | 0.006 | 0.0015 |
| 105 | Bus272 | Bus237 | 3352 | 1170 | 187.5 | 10.27 | 2.6 | 2974.8 | 1038.6 | 176.6 | 9.12 | 2.31 |
| 106 | UDUAGHAN I S/S | UDUAGHAN II S/S | 4220 | 1019 | 227.9 | 17.08 | 5.67 | 2127 | 748.7 | 126.6 | 5.27 | 1.75 |
| 107 | SOBOTE S/S | UDUAGHAN I S/S | 2074 | 731 | 115.4 | 4.7 | 1.56 | 1805.2 | 636.1 | 107.7 | 4.09 | 1.36 |
| 108 | SOBOTE S/S | SSS OFFICE S/S | 2063 | 727.4 | 115.1 | 3.11 | 1.03 | 1795.7 | 633 | 107.4 | 2.71 | 0.899 |
| 109 | SSS OFFICE S/S | Bus248 | 1826 | 643.8 | 102 | 3.42 | 1.14 | 1588.8 | 560.3 | 95.14 | 2.98 | 0.988 |
| 110 | Bus248 | ALUME DRIVE S/S | 642.3 | 225.5 | 35.93 | 0.273 | 0.0906 | 559 | 196.2 | 33.52 | 0.238 | 0.0789 |
| 111 | ALUME DRIVE S/S | NEW SSG S/S | 412.8 | 144.9 | 23.1 | 0.295 | 0.0746 | 359.2 | 126.1 | 21.55 | 0.256 | 0.0649 |
| 112 | NEW SSG S/S | ONWUKA ST. S/S | 271.3 | 96.44 | 15.21 | 0.113 | 0.0285 | 236.1 | 83.93 | 14.19 | 0.098 | 0.0248 |
| 113 | Bus248 | Bus255 | 824.7 | 293.8 | 46.21 | 0.426 | 0.142 | 717.7 | 255.7 | 43.11 | 0.371 | 0.123 |
| 114 | Bus255 | MARCULEY II S/S | 313.6 | 112.8 | 17.6 | 0.0546 | 0.0181 | 272.9 | 98.19 | 16.42 | 0.048 | 0.0158 |
| 115 | Bus255 | VICTOR OCHIE S/S | 510.6 | 180.8 | 28.61 | 0.216 | 0.0718 | 444.4 | 157.4 | 26.69 | 0.188 | 0.0625 |
| 116 | VICTOR OCHIE S/S | JAMES IBORI S/S | 304.5 | 108.9 | 17.09 | 0.072 | 0.0239 | 265 | 94.78 | 15.94 | 0.063 | 0.0208 |
| 117 | JAMES IBORI S/S | FITMAURICE ESTATE S/S | 6.15 | 2.03 | 0.342 | 0 | 0 | 5.35 | 1.77 | 0.319 | 0 | 0 |
| 118 | SSS I S/S | Bus248 | 355.2 | 123.3 | 19.85 | 0.121 | 0.0308 | 309.1 | 107.3 | 18.51 | 0.106 | 0.0268 |
| 119 | SSS I S/S | MARCULEY I S/S | 131.3 | 44.83 | 7.323 | 0.0296 | 0.0075 | 114.2 | 39.01 | 6.832 | 0.026 | 0.0065 |
| 120 | EBUBE S/S | Bus272 | 3283 | 1147 | 184.2 | 11.02 | 2.79 | 2913.7 | 1018.2 | 173.5 | 9.78 | 2.47 |
| 121 | EBUBE S/S | AIRTELS S/S | 81.19 | 28.66 | 4.575 | 0.0102 | 0.0026 | 72.05 | 25.43 | 4.31 | 0.009 | 0.0023 |
| 122 | INFANT JESUS II S/S | EBUBE S/S | 2940 | 1027 | 165.4 | 24 | 6.08 | 2608.9 | 911.4 | 155.9 | 21.3 | 5.39 |
| 123 | INFANT JESUS I S/S | ELGREEN HOTEL S/S | 2333 | 815.5 | 132.9 | 3.58 | 0.907 | 2070.5 | 723.7 | 125.2 | 3.18 | 0.805 |
| 124 | IKECHUKWU HOUSE S/S | INFANT JESUS II S/S | 2643 | 923.8 | 149.9 | 4.38 | 1.11 | 2345.6 | 819.8 | 141.3 | 3.89 | 0.984 |
| 125 | INFANT JESUS SCH. GAT S/S | CHYZ PETRO. S/S | 2069 | 725.1 | 118.4 | 1.71 | 0.432 | 1836.5 | 643.5 | 111.5 | 1.51 | 0.383 |
| 126 | CHYZ PETRO. S/S | LEASURE HOME S/S | 2121 | 742 | 121.1 | 3.21 | 0.814 | 1881.9 | 658.5 | 114.1 | 2.85 | 0.722 |
| 127 | LEASURE HOME S/S | INFANT JESUS I S/S | 2128 | 744.2 | 121.4 | 2.63 | 0.666 | 1888.5 | 660.5 | 114.3 | 2.33 | 0.591 |
| 128 | Bus306 | ANWAI GRA II S/S | 1237 | 434 | 70.9 | 1.71 | 0.434 | 1097.5 | 385.2 | 66.79 | 1.52 | 0.385 |
| 129 | ANWAI GRA II S/S | INFANT JESUS SCH S/S | 1463 | 513.6 | 83.84 | 0.228 | 0.0578 | 1298.1 | 455.8 | 78.99 | 0.203 | 0.0513 |
| 130 | INFANT JESUS SCH S/S | INFANT JESUS SCH. GAT S/S | 1756 | 616.2 | 100.5 | 2.05 | 0.519 | 1558.5 | 546.9 | 94.72 | 1.82 | 0.461 |
| 131 | PHASE II COMMUNITY S/S | INFANT JESUS SCH S/S | 240.1 | 84.89 | 13.78 | 0.272 | 0.0903 | 213.1 | 75.34 | 12.98 | 0.241 | 0.0801 |
| 132 | ANWAI RIVER S/S | Bus306 | 639.8 | 225.9 | 36.75 | 0.11 | 0.0278 | 567.8 | 200.5 | 34.62 | 0.097 | 0.0246 |
| 133 | Bus306 | Bus307 | 595.2 | 207.7 | 34.15 | 0.199 | 0.0503 | 528.2 | 184.3 | 32.17 | 0.176 | 0.0447 |
| 134 | Bus307 | IBORI GOLF I S/S | 214.1 | 74.88 | 12.29 | 0.0515 | 0.013 | 190 | 66.46 | 11.58 | 0.046 | 0.0116 |
| 135 | IBORI GOLF I S/S | MOCIWS S/S | 5.84 | 1.93 | 0.334 | 0.0001 | 0 | 5.19 | 1.71 | 0.314 | 1E-04 | 0 |
| 136 | Bus307 | IBORI GOLF II S/S | 380.9 | 132.8 | 21.85 | 0.163 | 0.0412 | 338 | 117.8 | 20.59 | 0.145 | 0.0366 |
| 137 | JASMINE SCHOOL S/S | IBORI GOLF II S/S | 47.02 | 16.14 | 2.695 | 0.0122 | 0.004 | 41.73 | 14.32 | 2.539 | 0.011 | 0.0036 |
| 138 | ANWAI CAMPUS S/S | ANWAI RIVER S/S | 385.6 | 135.6 | 22.15 | 1.31 | 0.332 | 342.2 | 120.4 | 20.86 | 1.16 | 0.294 |
| 139 | MTN CAMPUS S/S | ANWAI CAMPUS S/S | 5.81 | 1.92 | 0.333 | 0.0001 | 0 | 5.16 | 1.7 | 0.313 | 1E-04 | 0 |
| 140 | Bus10 | MTN I S/S | 71.35 | 24.97 | 4.005 | 0.0013 | 0.0003 | 65.85 | 23.04 | 3.848 | 0.001 | 0.0003 |
| 141 | Bus18 | DSEIRE & LEASURE S/S | 111.1 | 38.34 | 6.225 | 0.0091 | 0.003 | 101.2 | 34.93 | 5.942 | 0.008 | 0.0028 |
| 142 | Bus69 | UMUAGU I S/S | 280.7 | 100 | 15.73 | 0.0602 | 0.0152 | 234.3 | 83.5 | 14.37 | 0.05 | 0.0127 |
| 143 | STARCOM S/S | Bus87 | 2612 | 954.8 | 146 | 0.501 | 0.0953 | 4264.7 | 1484.1 | 262.7 | 1.62 | 0.308 |
| 144 | Bus122 | BENCLINTON S/S | 109.9 | 37.91 | 6.167 | 0.0043 | 0.0011 | 87.1 | 30.05 | 5.491 | 0.003 | 0.0009 |
| 145 | Bus172 | BAKARE S/S | 221.1 | 77.56 | 12.48 | 0.0173 | 0.0025 | 172.2 | 60.4 | 11.01 | 0.014 | 0.002 |
| 146 | Bus1 | ANWAI I S/S | 1115 | 8.6 | 58.74 | 1.12 | 0.284 | 826.5 | 287.6 | 48.38 | 0.76 | 0.192 |
| 147 | DESIRE&LESURE GARDEN S/S | Bus2 | 154.2 | 54.16 | 8.601 | 0.0188 | 0.0028 | 139.3 | 48.95 | 8.177 | 0.017 | 0.0025 |
| 148 | Bus272 | MIKE OKECHUKWU S/S | 58.64 | 20.29 | 3.286 | 0.0053 | 0.001 | 52.04 | 18.01 | 3.096 | 0.005 | 0.0009 |
| 149 | ELGREEN HOTEL S/S | IKECHUKWU HOUSE S/S | 2462 | 859.7 | 139.9 | 5.4 | 1.37 | 2184.7 | 763 | 131.8 | 4.79 | 1.21 |
| 150 | CHINEDU OKO S/S | CHINEDU OKO | 129.8 | 45.15 | 7.263 | 2.12 | 3.19 | 119.1 | 41.44 | 6.959 | 1.95 | 2.93 |
| 151 | CHYKES S/S | CHYKES | 273.6 | 97.34 | 15.34 | 6.32 | 9.48 | 247.2 | 87.94 | 14.58 | 5.71 | 8.57 |
| 152 | CHYZ PETRO. S/S | CHYZ PETRO. | 47.94 | 16.11 | 2.73 | 0.3 | 0.45 | 42.54 | 14.29 | 2.572 | 0.266 | 0.4 |
| 153 | DAVNOTCH S/S | DAVNOTCH | 224.8 | 78.88 | 12.61 | 4.27 | 6.41 | 213.1 | 74.8 | 12.28 | 4.05 | 6.07 |
| 154 | DSEIRE & LEASURE S/S | DESIRE & LEASURE | 111.1 | 38.34 | 6.225 | 1.56 | 2.34 | 101.2 | 34.93 | 5.942 | 1.42 | 2.13 |
| 155 | Bus2 | DESIRE&LESURE GARDEN | 154.2 | 54.16 | 8.601 | 2.98 | 4.47 | 139.3 | 48.95 | 8.177 | 2.69 | 4.04 |
| 156 | EBUBE S/S | EBUBE | 251.3 | 88.89 | 14.16 | 5.38 | 8.08 | 223 | 78.89 | 13.34 | 4.78 | 7.17 |
| 157 | ECOBANK S/S | ECOBANK | 21.88 | 7.26 | 1.22 | 0.0599 | 0.0899 | 20.51 | 6.81 | 1.181 | 0.056 | 0.0843 |
| 158 | ELGREEN HOTEL S/S | ELGREEN HOTEL | 123.3 | 42.86 | 7.019 | 1.98 | 2.98 | 109.4 | 38.04 | 6.612 | 1.76 | 2.64 |
| 159 | ENGR. ENENMOH S/S | ENGR. ENENMOH | 67.81 | 22.97 | 3.79 | 0.579 | 0.868 | 52.28 | 17.71 | 3.328 | 0.446 | 0.669 |
| 160 | FAVORITE S/S | FAVORITE | 91.76 | 31.4 | 5.128 | 1.06 | 1.59 | 87.01 | 29.77 | 4.994 | 1 | 1.51 |
| 161 | FIRS S/S | FIRS | 6.14 | 2.03 | 0.342 | 0.0094 | 0.0141 | 5.75 | 1.9 | 0.331 | 0.009 | 0.0132 |
| 162 | FITMAURICE ESTATE S/S | FITMAURICE ESTATE | 6.15 | 2.03 | 0.342 | 0.0094 | 0.0141 | 5.35 | 1.77 | 0.319 | 0.008 | 0.0123 |
| 163 | FMC S/S | FMC | 361.4 | 126.5 | 20.28 | 6.63 | 9.94 | 324.1 | 113.5 | 19.21 | 5.94 | 8.92 |
| 164 | FUNNAYA S/S | FUNNAYA | 261.5 | 92.62 | 14.57 | 5.7 | 8.55 | 213 | 75.43 | 13.15 | 4.64 | 6.96 |
| 165 | GOVERNMENT CORE AREA INJ. | GOVERNMENT CORE ASABA | 868.7 | 1702 | 33.43 | 0.729 | 14.59 | 16490 | 7014 | 313.5 | 64.14 | 1282.9 |
| 166 | HELIUS TOWER S/S | HELIUS TOWER | 68.04 | 23.74 | 3.814 | 1.17 | 1.76 | 59.16 | 20.64 | 3.556 | 1.02 | 1.53 |
| 167 | HILIOUS TOWER S/S | HILIOUS TOWER | 81.36 | 28.69 | 4.547 | 1.67 | 2.5 | 71.75 | 25.3 | 4.27 | 1.47 | 2.2 |
| 168 | IBORI GOLF I S/S | IBORI GOLF I | 208.2 | 72.94 | 11.96 | 3.84 | 5.76 | 184.8 | 64.73 | 11.26 | 3.41 | 5.11 |
| 169 | IBORI GOLF II S/S | IBORI GOLF II | 333.7 | 116.6 | 19.16 | 5.91 | 8.87 | 296.1 | 103.5 | 18.05 | 5.25 | 7.87 |
| 170 | IBUSA RD I S/S | IBUSA RD I | 355.1 | 124.3 | 20.11 | 6.51 | 9.77 | 276.5 | 96.83 | 17.74 | 5.07 | 7.61 |
| 171 | ICON S/S | ICON | 288.9 | 103.3 | 16.3 | 7.13 | 10.69 | 226.5 | 81 | 14.43 | 5.59 | 8.39 |
| 172 | IKECHUKWU HOUSE S/S | IKECHUKWU HOUSE | 177 | 62.95 | 10.08 | 4.09 | 6.13 | 157 | 55.87 | 9.491 | 3.63 | 5.44 |
| 173 | INALU I S/S | INALU I | 509 | 182.5 | 28.38 | 12.98 | 19.46 | 384.1 | 137.7 | 24.65 | 9.79 | 14.69 |
| 174 | INALU II S/S | INALU II | 258.3 | 91.49 | 14.48 | 5.63 | 8.45 | 198.2 | 70.22 | 12.69 | 4.32 | 6.48 |
| 175 | INFANT JESUS I S/S | INFANT JESUS I | 201.5 | 70.37 | 11.49 | 3.54 | 5.32 | 178.8 | 62.45 | 10.82 | 3.15 | 4.72 |
| 176 | INFANT JESUS II S/S | INFANT JESUS II | 272.6 | 97.15 | 15.5 | 6.45 | 9.67 | 241.9 | 86.22 | 14.6 | 5.72 | 8.59 |
| 177 | INFANT JESUS SCH S/S | INFANT JESUS SCH | 51.2 | 17.23 | 2.922 | 0.344 | 0.516 | 45.44 | 15.29 | 2.753 | 0.305 | 0.458 |
| 178 | INFANT JESUS SCH. GAT S/S | INFANT JESUS SCH. GAT | 311.6 | 108.4 | 17.83 | 5.12 | 7.68 | 276.6 | 96.22 | 16.79 | 4.54 | 6.81 |
| 179 | JAMES IBORI S/S | JAMES IBORI | 298.3 | 106.9 | 16.74 | 7.53 | 11.29 | 259.6 | 93 | 15.62 | 6.55 | 9.83 |
| 180 | JASMINE SCHOOL S/S | JASMINE SCHOOL | 47.01 | 16.14 | 2.695 | 0.585 | 0.877 | 41.72 | 14.32 | 2.539 | 0.519 | 0.779 |
| 181 | JOBAS S/S | JOBAS | 254.8 | 90.21 | 14.32 | 5.51 | 8.26 | 235.2 | 83.26 | 13.76 | 5.08 | 7.63 |
| 182 | LEASURE HOME S/S | LEASURE HOME | 4.74 | 1.56 | 0.269 | 0.0029 | 0.0044 | 4.2 | 1.38 | 0.253 | 0.003 | 0.0039 |
| 183 | MARCULEY I S/S | MARCULEY I | 131.2 | 44.82 | 7.323 | 1.44 | 2.16 | 114.2 | 39 | 6.832 | 1.25 | 1.88 |
| 184 | MARCULEY II S/S | MARCULEY II | 313.6 | 112.8 | 17.6 | 8.32 | 12.48 | 272.9 | 98.17 | 16.42 | 7.24 | 10.86 |
| 185 | MIKE OKECHUKWU S/S | MIKE OKECHUKWU | 58.64 | 20.29 | 3.286 | 0.87 | 1.3 | 52.04 | 18.01 | 3.096 | 0.772 | 1.16 |
| 186 | MOCIWS S/S | MOCIWS | 5.84 | 1.93 | 0.334 | 0.009 | 0.0134 | 5.19 | 1.71 | 0.314 | 0.008 | 0.0119 |
| 187 | MTN ANWAI RD S/S | MTN ANWAI RD | 59.29 | 20.52 | 3.305 | 0.88 | 1.32 | 53.7 | 18.58 | 3.145 | 0.797 | 1.19 |
| 188 | MTN CAMPUS S/S | MTN CAMPUS | 5.81 | 1.92 | 0.333 | 0.0089 | 0.0134 | 5.16 | 1.7 | 0.313 | 0.008 | 0.0119 |
| 189 | MTN I S/S | MTN I | 71.35 | 24.97 | 4.005 | 1.29 | 1.94 | 65.85 | 23.04 | 3.848 | 1.19 | 1.79 |
| 190 | MTN II S/S | MTN II | 57.53 | 19.89 | 3.222 | 0.836 | 1.25 | 50.31 | 17.39 | 3.014 | 0.731 | 1.1 |
| 191 | MTN III S/S | MTN III | 6.13 | 2.04 | 0.341 | 0.0188 | 0.0282 | 5.19 | 1.72 | 0.314 | 0.016 | 0.0238 |
| 192 | MTN IV S/S | MTN IV | 6.08 | 2.02 | 0.34 | 0.0186 | 0.0279 | 4.82 | 1.6 | 0.303 | 0.015 | 0.0221 |
| 193 | MTN V S/S | MTN V | 6.11 | 2.03 | 0.341 | 0.0187 | 0.0281 | 4.71 | 1.56 | 0.299 | 0.014 | 0.0216 |
| 194 | MTV VI S/S | MTV VI | 1.2 | 0.001 | 0.064 | 0.0007 | 0.001 | 0.938 | 0.0008 | 0.057 | 5E-04 | 0.0008 |
| 195 | NDDC S/S | NDDC | 236.5 | 83.25 | 13.25 | 4.71 | 7.07 | 200.2 | 70.47 | 12.19 | 3.99 | 5.99 |
| 196 | NEW SSG S/S | NEW SSG | 141.2 | 48.37 | 7.888 | 1.67 | 2.51 | 122.9 | 42.1 | 7.358 | 1.45 | 2.18 |
| 197 | NWOBOSHI S/S | NWOBOSHI | 206.3 | 72 | 11.56 | 3.59 | 5.38 | 195.6 | 68.28 | 11.26 | 3.4 | 5.11 |
| 198 | ODIACHI I S/S | ODIACHI I | 227.5 | 77.81 | 12.7 | 2.6 | 3.9 | 192.5 | 65.87 | 11.69 | 2.2 | 3.3 |
| 199 | ODIACHI II S/S | ODIACHI II | 221.2 | 77.52 | 12.39 | 4.12 | 6.18 | 187.2 | 65.62 | 11.4 | 3.49 | 5.23 |
| 200 | OGBEAMAI S/S | OGBEAMAI | 383.9 | 135.1 | 21.75 | 7.62 | 11.43 | 298.9 | 105.2 | 19.2 | 5.94 | 8.9 |
| 201 | OGBEKE SQ. S/S | OGBEKE SQ. | 384.3 | 135.3 | 21.8 | 7.65 | 11.48 | 299.3 | 105.4 | 19.24 | 5.96 | 8.94 |
| 202 | OKECHUKWU OKAFOR S/S | OKECHUKWU OKAFOR | 72.58 | 25.39 | 4.039 | 1.31 | 1.97 | 59.11 | 20.68 | 3.645 | 1.07 | 1.61 |
| 203 | OKELUE S/S | OKELUE | 206.8 | 72.18 | 11.58 | 3.6 | 5.4 | 177.1 | 61.82 | 10.71 | 3.08 | 4.62 |
| 204 | ONAJEI S/S | ONAJEI | 225.3 | 79.18 | 12.78 | 4.39 | 6.58 | 175.4 | 61.66 | 11.28 | 3.41 | 5.12 |
| 205 | ONOCHIE S/S | ONOCHIE | 287 | 102.5 | 16.12 | 6.98 | 10.46 | 247.2 | 88.29 | 14.96 | 6.01 | 9.01 |
| 206 | ONWUKA ST. S/S | ONWUKA ST. | 271.2 | 96.41 | 15.21 | 6.21 | 9.32 | 236 | 83.9 | 14.19 | 5.41 | 8.11 |
| 207 | PARKISON S/S | PARKISON | 334.9 | 116.8 | 18.83 | 5.71 | 8.56 | 265.5 | 92.55 | 16.76 | 4.53 | 6.79 |
| 208 | PHASE II COMMUNITY S/S | PHASE II COMMUNITY | 239.9 | 84.8 | 13.78 | 5.09 | 7.64 | 212.9 | 75.26 | 12.98 | 4.52 | 6.78 |
| 209 | SKY LYN HOTEL S/S | SKY LYN HOTEL | 68.54 | 23.91 | 3.828 | 1.18 | 1.77 | 62.2 | 21.7 | 3.646 | 1.07 | 1.61 |
| 210 | SOBOTE S/S | SOBOTE | 6.2 | 2.05 | 0.344 | 0.0095 | 0.0143 | 5.4 | 1.78 | 0.321 | 0.008 | 0.0124 |
| 211 | SPC S/S | SPC | 379.9 | 133.5 | 21.33 | 7.33 | 11 | 345.5 | 121.4 | 20.34 | 6.67 | 10 |
| 212 | SSS I S/S | SSS I | 223.8 | 78.49 | 12.52 | 4.21 | 6.31 | 194.8 | 68.31 | 11.68 | 3.66 | 5.5 |
| 213 | SSS OFFICE S/S | SSS OFFICE | 234.7 | 82.55 | 13.11 | 4.61 | 6.92 | 204.3 | 71.84 | 12.23 | 4.01 | 6.02 |
| 214 | ST. JOSEPH S/S | ST. JOSEPH | 252.9 | 89.57 | 14.3 | 5.49 | 8.24 | 197 | 69.75 | 12.62 | 4.28 | 6.41 |
| 215 | STADIUM OFFICE S/S | STADIUM OFFICE | 298.6 | 107 | 16.78 | 7.56 | 11.34 | 239 | 85.65 | 15.02 | 6.05 | 9.08 |
| 216 | STADIUM S/S | STADIUM | 427.5 | 151.4 | 24.06 | 9.33 | 13.99 | 338.3 | 119.8 | 21.41 | 7.38 | 11.07 |
| 217 | STARCOM S/S | STARCOM | 4.99 | 1.64 | 0.276 | 0.0031 | 0.0046 | 4.07 | 1.34 | 0.249 | 0.003 | 0.0037 |
| 218 | TEMPO CLINIC I S/S | TEMPO CLINIC I | 229.4 | 78.51 | 12.82 | 2.65 | 3.97 | 210.6 | 72.06 | 12.28 | 2.43 | 3.65 |
| 219 | TEMPO CLINIC II S/S | TEMPO CLINIC II | 216.5 | 75.77 | 12.13 | 3.95 | 5.92 | 198.7 | 69.55 | 11.62 | 3.63 | 5.44 |
| 220 | TOBI I S/S | TOBI I | 234.3 | 82.42 | 13.13 | 4.63 | 6.94 | 216.8 | 76.27 | 12.63 | 4.28 | 6.42 |
| 221 | TOBI II S/S | TOBI II | 221.1 | 77.48 | 12.35 | 4.1 | 6.15 | 200.7 | 70.31 | 11.77 | 3.72 | 5.58 |
| 222 | UDUAGHAN I S/S | UDUAGHAN I | 363.7 | 127.3 | 20.23 | 6.59 | 9.88 | 316.5 | 110.8 | 18.87 | 5.73 | 8.6 |
| 223 | UDUAGHAN II S/S | UDUAGHAN II | 211.3 | 73.84 | 11.8 | 3.74 | 5.61 | 186.4 | 65.12 | 11.08 | 3.3 | 4.94 |
| 224 | UMUAGU I S/S | UMUAGU I | 280.7 | 100 | 15.73 | 6.64 | 9.96 | 234.3 | 83.49 | 14.37 | 5.54 | 8.31 |
| 225 | UMUAGU II S/S | UMUAGU II | 330.1 | 119.3 | 18.52 | 9.21 | 13.82 | 275.5 | 99.56 | 16.92 | 7.69 | 11.53 |
| 226 | USONIA HOUSE S/S | USONIA HOUSE | 120.7 | 41.82 | 6.757 | 1.84 | 2.76 | 104.6 | 36.23 | 6.29 | 1.59 | 2.39 |
| 227 | VICTOR OCHIE S/S | VICTOR OCHIE | 205.9 | 71.86 | 11.52 | 3.56 | 5.35 | 179.2 | 62.53 | 10.75 | 3.1 | 4.65 |
| 228 | WATER BOARD S/S | WATER BOARD | 1.23 | 0.404 | 0.068 | 0.0001 | 0.0002 | 1.13 | 0.372 | 0.066 | 1E-04 | 0.0002 |
| 229 | ZANZIBAR S/S | ZANZIBAR | 97.76 | 33.52 | 5.429 | 1.19 | 1.78 | 87.94 | 30.15 | 5.149 | 1.07 | 1.6 |
|  | TOTAL LOSSES |  |  |  |  | 565.09 | 596.16 |  |  |  | 1329 | 2031.2 |

Figure 3: Section of the Modelled Single Line Diagram of Network of Study on ETAP 12.6 Edit Modes.

Figure 3: Section of the Modelled Single Line Diagram of Network of Study on ETAP 12.6 Edit Modes.

Figure 4:  Section of Network diagram of load flow analyses without DG on ETAP 12.6

Figure 5: Bus ID versus Loss sensitivity factor.

Table 2: Power loss Reduction before and after DG placement.

| Power loss | Before DG placement | After DG placement | % Reduction |
| --- | --- | --- | --- |
| Active(kW) | 1329.08 | 565.09 | 57.5 |
| Reactive(kVar) | 2031.16 | 596.16 | 70.7 |

5. DISCUSSION OF RESULTS

The results presented in Table 1 and 2, as well as Figures 4 and 6, show the real and reactive power flow, together with the associated line losses in the network. Figure 3 presents an extract from the load flow analysis of the power network, illustrating sections of the voltage limits across the various buses of the Benin Electricity Distribution Company (BEDC) Asaba 33/11kV 2 × 15MVA injection substation. The power flow analysis revealed that, within the statutory voltage range of 394.25V to 435.75V (0.95 p.u to 1.05 p.u), which is the acceptable voltage limit for distribution networks in Nigeria, only ten (10) out of the ninety-six (96) buses in the network operated within the permissible range, largely due to their proximity to the injection substation. The remaining eighty-six (86) buses were found to be operating outside the statutory voltage limits. In addition, the total active and reactive power losses in the network were determined to be 1,329.08 kW and 2,031.16 kVAr, respectively.

To compensate for and mitigate these losses, as well as to determine the priority order for candidate buses suitable for DG installation, the loss sensitivity factor for optimal DG placement and sizing was calculated using Equations (6) and (13). Based on reactive power demand, voltage magnitude, and network resistance, eleven (11) candidate buses were identified, as shown in Figure 5. The DG placement process was then carried out according to the loss sensitivity ranking in order to determine the optimal locations and sizes. A total DG capacity of 16 MW was integrated into the distribution network, and its most significant impact was observed when allocated across Uduaghan I (2.3 MW),

Figure 6: Section of Network diagram of load flow analyzes with DG placement on ETAP 12.6

Section

Figure 6: Network diagram of load flow analyses with DG placement on ETAP 12.6

Figure 7: Power loss Reduction before and after DG placement.

Figure 8: Percentage Reduction of Power loss after DG placement.

Anwai Campus (3.7 MW), Budget (4.0 MW), and Inalu I (6.0 MW), in accordance with the optimal placement and sizing algorithm. The comparative results before and after DG integration, presented in Tables 1 and 2 as well as Figures 4 and 6, show significant improvements in network performance. After DG installation, ninety-one (91) out of ninety-six (96) buses operated within the statutory voltage limits, while only five (5) buses remained outside the acceptable range. Furthermore, the active power losses were reduced by 57.5%, decreasing from 1,329.08 kW to 565.09 kW, while the reactive power losses were reduced by 70.7%, decreasing from 2,031.16 kVAr to 596.16 kVAr, as shown in Table 2 and Figure 7 and 8.

These results demonstrate that the optimal placement and sizing of DG units play a significant role in minimising active and reactive power losses, improving voltage regulation, enhancing system reliability, increasing operational efficiency, and maintaining overall network stability. The integration of DG therefore had a positive impact on the overall power flow performance of the network under study.

6. CONCLUSION

This research evaluated the impact of distributed generation on the Benin Electricity Distribution Company (BEDC) Asaba 33/11kV 2 × 15MVA injection substation, with the aim of mitigating network violations and reducing power losses through the integration of distributed generation. The results obtained show that the optimal placement and sizing of DG units significantly improve voltage profiles across the distribution network while substantially reducing power losses. The integration of DG enabled additional power injection into the network, thereby enhancing overall system performance. Based on these findings, it is recommended that the network under study should be upgraded to fully realise the benefits of distributed generation. Furthermore, stakeholders and government at all levels in Nigeria should prioritise, encourage, and invest in distributed generation, particularly renewable energy-based DG systems, due to their abundance, environmental sustainability, and ability to improve network performance when optimally integrated.

REFERENCES

[1] International Energy Agency, World Energy Outlook 2025, Paris, France, 2025.

[2] World Bank, Tracking SDG7: The Energy Progress Report, Washington, DC, USA, 2024.

[3] Federal Ministry of Power, Electric Power Sector Reform Act Implementation Report, Abuja, Nigeria, 2025.

[4] Nigerian Electricity Regulatory Commission, Nigerian Electricity Industry Performance Report, Abuja, Nigeria, 2025.

[5] International Renewable Energy Agency, Global Energy Statistics 2025, Abu Dhabi, UAE, 2025.

[6] D. O. Akinyele, R. K. Rayudu, and N. K. C. Nair, “Global progress in photovoltaic technologies and Nigerian energy applications,” Renewable and Sustainable Energy Reviews, vol. 48, pp. 112–139, 2015.

[7] T. Ackermann, G. Andersson, and L. Söder, “Distributed generation: A definition,” Electric Power Systems Research, vol. 57, no. 3, pp. 195–204, 2001.

[8] D. Singh and S. K. Goswami, “Optimum allocation of distributed generations based on nodal pricing,” IEEE Transactions on Power Systems, vol. 25, no. 4, pp. 2021–2028, 2010.

[9] D. Q. Hung, N. Mithulananthan, and R. C. Bansal, “Analytical expressions for DG allocation in primary distribution networks,” IEEE Transactions on Energy Conversion, vol. 25, no. 3, pp. 814–820, 2010.

[10] V. H. Méndez Quezada, J. Rivier Abbad, and A. Gómez Expósito, “Assessment of energy distribution losses for increasing penetration of distributed generation,” IEEE Transactions on Power Systems, vol. 21, no. 2, pp. 533–540, 2006.

[11] N. Acharya, P. Mahat, and N. Mithulananthan, “An analytical approach for DG allocation in primary distribution network,” International Journal of Electrical Power & Energy Systems, vol. 28, no. 10, pp. 669–678, 2006.

[12] T. Gözel and M. H. Hocaoglu, “An analytical method for the sizing and siting of distributed generators in radial systems,” Electric Power Systems Research, vol. 79, no. 6, pp. 912–918, 2009.

[13] N. S. Rau and Y. H. Wan, “Optimum location of resources in distributed planning,” IEEE Transactions on Power Systems, vol. 9, no. 4, pp. 2014–2020, 1994.

[14] D. Q. Hung and N. Mithulananthan, “Multiple distributed generator placement in primary distribution networks,” IEEE Transactions on Industrial Electronics, vol. 60, no. 4, pp. 1708–1717, 2013.

[15] Y. M. Atwa, E. F. El-Saadany, M. M. A. Salama, and R. Seethapathy, “Optimal renewable resources mix for distribution system energy loss minimisation,” IEEE Transactions on Power Systems, vol. 25, no. 1, pp. 360–370, 2010.

[16] M. H. Moradi and M. Abedini, “A combination of genetic algorithm and particle swarm optimisation for optimal DG location and sizing,” International Journal of Electrical Power & Energy Systems, vol. 34, no. 1, pp. 66–74, 2012.

[17] Nwajuonye Raymond O, Okonkwo Innocent I, Iloh JP. Distribution Network Enhancement and Efficiency Improvement Using Distributed Generation. Journal of Engineering Research and Reports’’ 21(3): 55-71, 2021; Article no. JERR.76100 ISSN: 2582 - 2926.