Air Quality and Microbial Contamination of Hospital Environments in Warri and Its Environs

ABSTRACT

The quality of air in healthcare environments has become a major public health concern globally, particularly as it relates to the transmission of airborne diseases and hospital-acquired infections (HAIs). The study assessed the microbial contamination and air quality of selected hospital environments in Warri and its environs, with a focus on identifying the types and concentrations of airborne microorganisms, to determine their compliance with World Health Organization (WHO), National Environmental Standards and Regulations Enforcement Agency (NESREA), and Standards Organization of Nigeria (SON) guidelines. Airborne pollutants such as particulate matters (PM2.5 and PM10), carbon dioxide (CO2), volatile organic compounds (VOCs), methane (CH4), and microbial contaminants were measured using Aeroqual Series 500 monitors and passive culture plate exposure respectively. Results revealed elevated indoor temperatures (29.1°C–32.8°C) and poor ventilation in several departments, especially administrative and emergency units, which corresponded with higher pollutant levels. Hazardous levels of methane (up to 4381 ppm) and VOCs (up to 9458 ppm) were detected, far exceeding recommended indoor limits. Bacterial and fungal analyses identified Bacillus spp., Staphylococcus aureus, Proteus mirabilis, Enterobacter spp., and airborne fungi such as Aspergillus niger, Alternaria spp., and Rhizopus spp. The study established a positive correlation between poor indoor air quality indicators and elevated microbial loads, suggesting a significant risk for hospital-acquired infections (HAIs). These findings highlight the urgent need for continuous air monitoring, improved Heating, Ventilation and Air Conditioning (HVAC) systems, and targeted interventions such as High-Efficiency Particulate Air (HEPA) filtration and microbial surveillance, particularly in high-risk zones.

Keywords: Indoor Air Quality (IAQ), Microbial Contamination, Hospital Environments, Airborne Pathogens, Hospital-Acquired Infections (HAIs), Bioaerosols

Introduction

Indoor air quality (IAQ) in hospitals plays a central role in protecting patients, visitors, and healthcare workers from airborne pollutants and infectious agents. Hospitals differ from typical indoor environments because they host highly vulnerable individuals, including the elderly, surgical patients, newborns, and immunocompromised persons, all of whom are at heightened risk of airborne infections (Humphreys & Coleman, 2020). The hospital environment often contains a mixture of pollutants such as particulate matter (PM₂. ₅ and PM₁₀), volatile organic compounds (VOCs), and biological contaminants like bacteria, viruses, and fungal spores. These pollutants originate from outdoor air, cleaning agents, medical procedures, ventilation systems, and building materials (D’Alessandro et al., 2020). Fine particulate matter, especially PM₂. ₅, can carry pathogens deep into the lungs and enhance the risk of respiratory infections, while VOCs, though non-infectious, may irritate the respiratory tract and suppress immune defenses, increasing susceptibility to opportunistic infections (Li et al., 2007)

Bioaerosols produced through coughing, sneezing, talking, and aerosol-generating procedures can remain suspended in the air for long periods. These airborne microorganisms contribute substantially to hospital-acquired infections (HAIs), especially in crowded or poorly ventilated zones (Otter et al., 2021). Studies frequently detect Staphylococcus aureus, Pseudomonas aeruginosa, and Aspergillus fumigatus in hospital settings, particularly in areas with inadequate ventilation or high patient traffic. These pathogens can remain viable in indoor air, settle on surfaces, and contaminate medical equipment, posing significant health risks to patients recovering from surgery or those with weakened immunity (Kowalski, 2021).

Critical environments such as Intensive Care Units (ICUs), surgical theatres, Neonatal Intensive Care Units (NICUs), hematology wards, and transplant units require especially stringent air quality management. These units contain large numbers of immunocompromised individuals for whom even low concentrations of airborne pathogens can result in severe and potentially life-threatening infections. Airborne transmission has been implicated in outbreaks of diseases such as tuberculosis, influenza, invasive aspergillosis, and COVID-19, underscoring the need for robust air management systems (Beggs, 2022). Documented cases show that contaminated air ducts, inadequate filtration, and construction activities can introduce fungal spores into hospital air, triggering outbreaks of invasive aspergillosis particularly in hematology and oncology wards where patient immune defenses are significantly weakened (Eames et al., 2020; WHO, 2023).

Construction and renovation activities pose a unique threat by releasing dust and Aspergillus spores into the air. Without proper containment measures, these spores can infiltrate clinical areas and cause fatal fungal infections among vulnerable patients, especially those undergoing chemotherapy or stem cell transplantation (Beggs, 2022). Such events have prompted hospitals to adopt stricter infection-control measures, including HEPA-filtered ventilation systems, physical barriers, negative-pressure isolation rooms, and careful monitoring of airflow during building maintenance and construction (Azimi & Stephens, 2013).

Maintaining good IAQ is therefore fundamental to infection-prevention practices. Clean hospital air reduces airborne pathogen loads and supports other infection-control strategies such as proper hand hygiene, sterilization of medical equipment, and routine surface disinfection (Otter et al., 2021). Sorouri et al. (2025) considered hospital air pollution as a serious public health emergency because exposure affects both patient results and staff productivity. Air pollution in hospitals can compromise respiratory health, worsen asthma, increase cardiovascular stress, trigger allergies and facilitate airborne transmission of infectious diseases. Effective air quality management includes adequate ventilation, air filtration with HEPA filters, pressure zoning (positive pressure for operating rooms and negative pressure for isolation rooms), and continuous monitoring of airborne contaminants (Azimi & Stephens, 2013). Maintaining optimal temperature and humidity also enhances patient comfort and reduces microbial growth, contributing further to patient safety (D’Alessandro et al., 2020).

Poor indoor air quality is associated with increased rates of hospital-acquired infections such as ventilator-associated pneumonia, surgical site infections, and invasive fungal diseases, all of which increase treatment costs, prolong hospital stays, and elevate morbidity. Improving IAQ has been shown to reduce infection rates, promote faster recovery, and lower overall healthcare expenditures. According to the World Health Organization, comprehensive infection-prevention strategies including environmental interventions like enhanced air management can reduce hospital-acquired infections by up to 70% (WHO, 2023). Also, An et al. (2025) proved that air purifiers are also valuable tools for reducing airborne infection risk and protecting patients when strategically deployed. Thus, investing in-door hospital air quality is not only a preventive health measure but also an economically sound strategy that strengthens the overall quality of healthcare delivery (Humphreys & Coleman, 2020).

### The main aim of this study was to investigate the quality of indoor air and associated microbial contaminants in selected hospitals in Warri and its environs to evaluate compliance with regulatory standards and mitigate the risk of hospital-acquired infections.

### Materials and Methods

Study Area

This study was done on three major hospitals in Warri and its surroundings. These facilities have been selected due to their central deployment in healthcare delivery to the people, and the high number of patients served daily that might lead to indoor air pollution. The hospitals chosen included Hospitals 1 (Agbarho), Hospital 2 (Ekpan) and Hospital 3 (Warri). In every hospital, microbial plate exposure and indoor air quality monitoring were carried out in the strategically chosen locations in wards, outpatient waiting areas, and main entrances, provided they were accessible. These sites were chosen because they were representative of high traffic and clinically relevant places where airborne contamination is likely to take place. Three (3) departments were selected from each hospital, resulting in a total of nine departments assessed for indoor air quality in this study.

### Sample collection

Air quality analysis was carried out using the Aeroqual Series 500 portable air quality monitor, while microbial air sampling was conducted using nutrient agar and Sabouraud dextrose agar that were freshly prepared aseptically in the laboratory prior to field deployment. Agar plates were exposed to air at selected locations for 30 minutes to allow passive sedimentation of airborne microorganisms. After the 30 minutes exposure, the Agar plates were taken to the laboratory for microbial analyses. Analyses of air quality parameters were done in-situ. These complementary methods were designed to assess both the chemical and biological components of air quality within three selected hospitals within Warri and its environments

### Microbial Analyses

Air samples were collected using the passive sedimentation (settle plate) method, involving a 30-minute exposure of freshly prepared Nutrient Agar (NA) and Sabouraud Dextrose Agar (SDA) plates. Following exposure, the Nutrient Agar plates were incubated at 37 °C for 24–48 hours for the enumeration of total bacterial counts, while the Sabouraud Dextrose Agar plates were incubated at 25–28 °C for 3–7 days for fungal growth. (Alemayehu et al., 2022; Okafor et al., 2021). The microbial loads were subsequently determined using standard microbiological procedures for total bacterial and fungal counts, respectively.

#### Bacterial Identification

The identification of the isolates was based on the various physiological and biochemical tests carried out using Bergey’s Manual of Systemic Bacteriology (Haider et al., 2022).

#### Fungal Identification

The fungi were evaluated based on their airborne concentration (cfu/m³), the diversity of fungal species isolated, their spatial distribution across various hospital departments, and their level of compliance with WHO recommended standards for indoor air quality. (Shi et al., 2025; World Health Organization, 2009)

### Procedure for Operating the Aeroqual Air Quality Monitoring Equipment

The air quality measurements focused on key airborne pollutants, including particulate matter (PM2.5 and PM10) and gaseous pollutants such as ozone (O3), nitrogen dioxide (NO2), and volatile organic compounds (VOCs), depending on the sensor heads deployed. The Aeroqual Series 500 was calibrated according to the manufacturer’s specifications prior to each sampling session, and data were logged at predetermined intervals for later analysis (Aeroqual Ltd., 2021; Lin et al., 2015)

Statistical analysis

The collected data were analyzed through descriptive statistics, mean and standard deviation, to provide the summary of concentrations of pollutants in various sampling points. The findings were further compared by comparing the measured values to WHO/NESREA/SON permissible limits to determine compliance as well as spatial variation across hospital settings.

## Results and Discussion

The air quality assessment conducted across three hospitals in Delta State revealed notable variations in the concentration of major gaseous pollutants and volatile organic compounds (VOCs), as well as microclimatic factors such as temperature and wind speed. Table 1 shows measured air quality parameters in various departments of three selected hospitals in Warri and environs in comparison with WHO/NESRA/SON acceptable limits. Figures 1, 2, and 3 are charts showing the air quality readings at the different hospitals.

Table 1: Measured Air Quality Parameters in Various Departments of Three Selected Hospitals in Delta State in Comparison with WHO/NESRA/SON Acceptable Limits

| Parameter | WHO/NESREA/ SON | Hospital 1 Card/Record | Hospital 1 Antenatal | Hospital 1 Female ward | Hospital 2 Ultrasound | Hospital 2 Card/Records | Hospital 2 Physiotherapy | Hospital 3 Emergency | Hospital 3 Card/Records | Hospital 3 Female Ward |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Temp (°C) | 18–24 | 29. 1± 0.49 | 29.5±0.44 | 29.6 ± 0.71 | 31.2 ± 0.88 | 32.1 ± 0.68 | 32.4 ± 0.32 | 32.5±0.30 | 31.1± 0.21 | 32.8±0.56 |
| Wind Speed (mph) PM2.5 (ug/m3) PM10 (ug/m3) | — 15 45 | 0 .2 ± 0.00 30.7 46.3 | 0.0 ± 0.0 28.8 48.3 | 0.0± 0.0 29.8 51.8 | 0.0± 0.0 29.1 50.3 | 5.8 ± 0.09 28.8 48.8 | 4.6± 0.02 29.5 47.5 | 0.8± 0.014 19.0 31.1 | 0.0 ± 0.0 17.8 27.1 | 0.0±0.0 18.8 31.8 |
| NO2 (ppm) | 0.04 | 0.015 ± 0.0 | 0.019 ± 0.0 | 0.018± 0.0 | 0.012± 0.0 | 0.0± 0.0 | 0.0± 0.0 | 0.034 ± 0.0 | 0.021 ± 0.001 | 0.012±0.0 |
| SO2 (ppm) | 0.05 | 0.0 ± 0.0 | 0.0 ± 0.0 | 0.0 ± 0.0 | 0.0 ± 0.0 | 0.0 ± 0.0 | 0.0± 0.0 | 0.0 ± 0.0 | 0.0 ± 0.0 | 0.0 ± 0.0 |
| CH4 (ppm) | 10 | 2.87 ± 0.1 | 5.99 ± 0.1 | 2.08 ± 0.1 | 3.69± 0.1 | 2.44 ± 0.1 | 2.53 ± 0.1 | 3491 ± 76.8 | 2593 ± 41.9 | 4381±60.1 |
| H2S (ppm) | 0.008 | 0.31 ± 0.00 | 0.0 ± 0.0 | 0.0 ± 0.0 | 0.77 ± 0.00 | 0.26 ± 0.00 | 0.0 ± 0.0 | 0.0 ± 0.0 | 0.0 ± 0.0 | 0.0 ± 0.0 |
| CO (ppm) | 10 | 1.5 ± 0.02 | 1.2 ± 0.02 | 1.2± 0.02 | 0. 6± 0.00 | 1.72± 0.01 | 0.6 ± 0.01 | 1.7 ± 0.012 | 1.5 ± 0.031 | 1.2 ± 0.02 |
| VOC (ppm) | 600 | 9458 ± 87.5 | 1804±50.1 | 1890 ± 16.1 | 1756±43.2 | 1771 ± 19.4 | 1958 ± 39.4 | 2 731± 20.5 | 1791 ± 29.4 | 2982 ± 38.8 |

Note: All values are expressed as mean ± standard error.

The results show that temperature values across all three hospital ranged from 29.1 ± 0.49°C to 32.8 ± 0.56°C, which are above the WHO/NESREA/SON standard of 18–24°C. PM2.5 ranged from 0.0 to 5.8 µg/m³ and PM10 from 27.1 to 51.8 µg/m³, with some locations exceeding recommended limits. NO₂ levels ranged from 0.0 to 0.034 ppm, while SO₂ was not detected in all locations. CH₄ varied widely from 2.08 ± 0.1 to 4381 ± 60.1 ppm, H₂S from 0.0 to 0.77 ± 0.00 ppm, CO from 0.6 ± 0.00 to 1.72 ± 0.01 ppm, and VOCs from 1756 ± 43.2 to 9458 ± 87.5 ppm across the sampled hospital environments.

Figure 1: Chart Showing the Air Quality Readings at Hospital 1

Figure 2: Chart Showing the Particulate Matter Readings at Hospital 1

Figure 3:  Chart Showing the Air Quality Readings at Hospital 2

Figure 4:  Chart Showing the Particulate Matter Readings at Hospital 2

Figure 5:  Chart Showing the Air Quality Readings at Hospital 3

Figure 6:  Chart Showing the Particulate Matter Readings at Hospital 3

Table 2 shows variation in total bacterial counts across the sampled hospital departments, ranging from 0.23 ± 0.01 × 10² CFU/m³ to 5.29 ± 0.09 × 10³ CFU/m³. Hospital 3 Card/Records recorded the highest bacterial load, while Hospital 1 Antenatal Care showed one of the lowest values. The bacterial isolates identified across the locations include Bacillus spp., Staphylococcus aureus, Micrococcus spp., Proteus mirabilis, and Enterobacter spp. In general, most of the bacterial counts exceeded the WHO/NESREA/SON acceptable limit of ≤ 5.0 × 10² CFU/m³, with only a few departments falling within or close to the guideline value.

Table 2: Total Bacterial Load (CFU/m³) and Identified Bacterial Isolates Across Three Hospital Departments Compared with WHO, NESREA, and SON Standards

| Hospital | Department | Total Bacteria Count (CFU /m3) | WHO/NESREA /SON Acceptable Limit (CFU /m³) | Bacterial Isolates |
| --- | --- | --- | --- | --- |
| Hospital 1 | Card/ Records | 1.00±0.02 × 10³ | ≤ 5.0×10² | Bacillus spp |
|  | Antenatal Care | 0.23±0.01× 102 | ≤ 5.0×10² | Bacillus spp |
|  | Female Ward | 0.41±0.02× 102 | ≤ 5.0×10² | Staphylococcus aureus |
| Hospital 2 | Ultrasound | 1.67 ± 0.06 × 10³ | ≤ 5.0×10² | Proteus mirabilis; Bacillus spp |
|  | Card / Records | 0.38±0.02× 102 | ≤ 5.0×10² | Bacillus spp |
|  | Physiotherapy Centre | 0.32±0.01× 102 | ≤ 5.0×10² | Micrococcus spp |
| Hospital 3 | Emergency Ward (L3a) | 2.33 ± 0.05 × 10³ | ≤ 5.0×10² | Staph. aureus; Bacillus spp. |
|  | Card / Records (L3b) | 5.29 ± 0.09 × 10³ | ≤ 5.0×10² | Enterobacter spp; Bacillus spp; Staphylococcus aureus; Micrococcus spp. |
|  | Female Ward (L3c) | 0.45±× 102 | ≤ 5.0×10² | Staph. aureus; Bacillus spp |

Note: All values are expressed as mean± standard error. spp = species.

Table 3 shows variation in total fungal counts across the sampled hospital departments, ranging from 0.18 ± 0.01 × 10² CFU/m³ to 20.0 ± 0.23 × 10² CFU/m³. Hospital 3 Emergency Ward recorded the highest fungal load, while Hospital 1 Antenatal Care recorded one of the lowest values. The fungal isolates identified across the hospitals include Aspergillus flavus, Aspergillus niger, Rhizopus spp., Fusarium spp., and Alternaria spp.. Overall, most departments recorded fungal counts within or around the WHO permissible limit of ≤ 5.0 × 10² CFU/m³, with a few locations showing elevated values above the guideline threshold.

Table 3: Total Fungal Load (CFU/m³) and Identified Fungal Isolates Across Three Hospital Departments Compared with WHO Standards

| Hospital | Department | Total Fungi Count (CFU /m3) | WHO | Fungi Isolates |
| --- | --- | --- | --- | --- |
| Hospital 1 | Card / Records | 6.7 ± 0.09 × 10² | ≤ 5.0×10² | Aspergillus flavus; Rhizopus spp. |
|  | Antenatal Care | 0.18± 0.01 × 10² | ≤ 5.0×10² | Aspergillus niger |
|  | Female Ward | 0.22± 0.03 × 10² | ≤ 5.0×10² | Aspergillusflavus |
| Hospital 2 | Ultrasound | 0.20± 0.01 × 10² | ≤ 5.0×10² | Fusarium spp |
|  | Card / Records | 3.3 ± 0.06 × 10² | ≤ 5.0×10² | Aspergillus niger |
|  | Physiotherapy Centre | 0.31± 0.02 × 10² | ≤ 5.0×10² | Aspergillus niger |
| Hospital 3 | Emergency Ward | 20.0 ± 0.23 × 10² | ≤ 5.0×10² | Alternaria spp; Rhizopus spp. Aspergillus niger |
|  | Card / Records | 6.7± 0.07 × 10² | ≤ 5.0×10² | Fusarium spp |
|  | Female Ward | 0.40± 0.03 × 10² | ≤ 5.0×10² | Aspergillus niger |

Note: All values are expressed as mean± standard error. spp= species.

Air quality assessment across nine hospital departments showed substantial spatial variation when compared with WHO (2023), NESREA (2011), and SON (2015) standards. The physicochemical characteristics observed in this study are consistent with recent empirical evidence showing that hospital indoor environments often exhibit elevated temperature, particulate matter, and chemical pollutants. The temperature range recorded in this study (29.1–32.8°C) agrees with reports that hospital indoor temperatures in tropical and resource-limited settings frequently exceed recommended comfort limits. Similarly, the PM₁₀ values (27.1–51.8 µg/m³), with some exceeding the 45 µg/m³ guideline, align with findings from recent hospital-based studies that documented elevated particulate matter levels in clinical environments, particularly in high-activity units (Ahmad Jonidi Jafari et al., 2025). Furthermore, the extremely high VOC concentrations observed in this study (up to 9458 ppm) are consistent with broader reviews indicating that healthcare environments often contain significant levels of VOCs due to disinfectants, medical supplies, and cleaning agents (Morakinyo et al., 2022). These findings collectively reinforce the pattern that hospital indoor air is often chemically burdened and spatially variable.

The bacterial results of this study also show strong agreement with previous research demonstrating that hospital air commonly contains elevated microbial loads, especially in high-occupancy areas. The bacterial counts recorded in this study (up to 5.29 × 10³ CFU/m³) fall within the range reported in recent studies, where concentrations between 829 and 4980 CFU/m³ were observed in hospital wards and outpatient departments (Onmek et al., 2022). The dominance of Bacillus spp., Staphylococcus aureus, and Micrococcus spp. identified in this study further aligns with these findings, as these genera are consistently reported as the most abundant airborne bacteria in healthcare environments (Onmek et al., 2022). In addition, evidence from hospital-based exposure studies indicates that indoor bacterial aerosols are prevalent and may pose health risks in clinical settings, particularly in developing regions (Megri et al., 2022), supporting the elevated bacterial loads observed across several departments in this study.

The fungal findings equally agree with recent studies highlighting the widespread presence and variability of airborne fungi in hospital environments. The fungal counts recorded in this study (up to 20.0 × 10² CFU/m³) are comparable to values reported in hospital environments, where fungal concentrations ranging from 90 to 920 CFU/m³ have been documented (Onmek et al., 2022). The predominance of genera such as Aspergillus, Fusarium, and Alternaria also aligns with recent findings from hospital-based studies, which consistently identify these fungi as common airborne contaminants. For example, Belizario et al. (2021) reported that Aspergillus species are among the most dominant fungi in indoor hospital air, particularly in critical care areas. Similarly, Lemos et al. (2024) documented the frequent occurrence of Aspergillus species in tertiary hospital environments, with variations across departments. These findings support the fungal profile and spatial distribution observed in this study.

In addition to agreement, the present findings also show some variation compared with previous studies, highlighting the influence of environmental and operational factors. While some studies report consistently high particulate and microbial loads across all hospital units, this study shows that certain departments recorded lower PM₂.₅ and fungal counts, indicating localized differences. Recent reviews confirm that indoor air quality in hospitals is strongly influenced by ventilation efficiency, occupancy rate, and sanitation practices, with better managed environments showing reduced contamination levels (Morakinyo et al., 2022). This suggests that the variability observed in this study reflects the dynamic and location specific nature of hospital indoor air quality.

Overall, the findings of this study are in strong agreement with recent research, demonstrating that hospital indoor air is characterized by elevated chemical pollutants, significant microbial contamination, and marked spatial variability across departments. The concurrence of high VOC levels, elevated particulate matter, and substantial bacterial and fungal loads supports the growing body of evidence that healthcare environments remain critical zones for indoor air quality concerns. At the same time, the observed variations across departments reinforce the understanding that indoor air quality is not uniform but influenced by multiple interacting factors, highlighting the need for continuous monitoring and targeted environmental management in hospital settings.

# Conclusion

# This study reveals that the selected hospitals exhibit generally poor indoor air quality characterized by elevated temperatures, high particulate matter (PM₁₀), and significantly high volatile organic compound (VOC) concentrations that exceed recommended standards. The physicochemical findings indicate that hospital indoor environments are thermally stressed and chemically polluted, particularly in high-activity departments, which reflects potential inadequacies in ventilation and environmental control systems. The microbiological assessment further shows substantial bacterial and fungal contamination, with bacterial loads exceeding WHO/NESREA/SON limits in most departments and fungal isolates dominated by potentially pathogenic genera such as Aspergillus, Bacillus, Staphylococcus aureus, and Fusarium. These findings collectively imply that hospital indoor environments in the study area pose potential occupational and public health risks to patients, healthcare workers, and visitors due to continuous exposure to airborne pollutants and microbial contaminants. The study therefore underscores the urgent need for improved ventilation systems, routine air quality monitoring, and strict infection control and environmental hygiene practices to reduce airborne contamination and safeguard health within hospital settings.

Disclaimer (Artificial intelligence)

Author(s) hereby declare that NO generative AI technologies such as Large Language Models (ChatGPT, COPILOT, etc.) and text-to-image generators have been used during the writing or editing of this manuscript.

# References

Adams, R. I., Miletto, M., Taylor, J. W., & Bruns, T. D. (2013). Dispersal in microbes: Fungi in indoor air are dominated by outdoor air and show dispersal limitation at short distances. The ISME Journal, 7(7), 1262–1273.

Adekanmbi, A. O., & Falodun, O. E. (2015). Microbial quality of air in different hospital wards and outpatient departments. Journal of Applied Sciences and Environmental Management, 19(2), 183–189.

Ahmad Jonidi Jafari, A., Gholami, M., Arfaeinia, H., et al. (2025). Indoor air quality assessment in hospital environments: Concentration and health risk of particulate matter and gaseous pollutants. Scientific Reports.

Alemayehu, T., Getachew, H., & Feleke, B. (2022). Microbial air quality assessment in selected hospital wards in Ethiopia. PLOS ONE, 17(8), e0271022.

An, I.H., Kwak, D.B., Lee, J., Park, S.H., and Yook, S. J. (2025). Optimal operating positions of two air purifiers for improving indoor air quality in hospital wards. Journal of Hospital Infection, 159, 42-51.

Azimi, P., & Stephens, B. (2013). HVAC filtration for controlling infectious airborne disease transmission in indoor environments: Predicting risk reductions and operational costs. Building and Environment, 70, 150–160.

Beggs, C. B. (2022). The airborne transmission of infection in hospital buildings: Fact or fiction? Indoor and Built Environment, 31(1), 3–15.

Belizario, J. A., Lopes, L. G., & Pires, R. H. (2021). Fungi in the indoor air of critical hospital areas: A review. Aerobiologia, 37(3), 379–394.

Belizario, M. D., Gomes, G. P., Duarte, C. M., & Ferreira, F. A. (2021). Airborne fungal diversity in hospital environments: Health implications. Brazilian Journal of Microbiology, 52(4), 1891–1902.

D’Alessandro, D., Fabiani, M., Orsi, G. B., & Fara, G. M. (2020). Indoor air quality in hospitals: A review of the literature. Reviews on Environmental Health, 35(4), 463–472.

Eames, I., Shoaib, D., Klettner, C., & Taban, V. (2020). Movement of airborne contaminants in a hospital isolation room. Journal of the Royal Society Interface, 17(163), 20200018.

Ede, P. N., & Edokpa, D. O. (2020). Methane and hydrocarbon pollution in the Niger Delta: Implications for ambient air quality. Environmental Pollution Research Journal, 27(4), 220–230.

Ede, P. N., Nwogu, E. U., & Okocha, C. (2020). Assessment of indoor and outdoor air quality in healthcare facilities in southern Nigeria. International Journal of Environmental Monitoring and Analysis, 8(3), 61–70.

Efe, S. I. (2018). Urban climate and indoor thermal conditions in tropical hospitals. Nigerian Journal of Environmental Sciences and Technology, 2(1), 19–30.

Ekhaise, F. O., & Ogboghodo, B. I. (2011). Microbiological indoor and outdoor air quality of two major hospitals in Benin City, Nigeria. Sierra Leone Journal of Biomedical Research, 3(3), 169–174.

Ekhaise, F. O., Isitor, E. E., Ighosewe, O. U., & Emoghene, A. O. (2010). Airborne microflora in the atmosphere of a hospital environment of the University of Benin Teaching Hospital (UBTH), Benin City, Nigeria. World Journal of Agricultural Sciences, 6(2), 166–170.

Haider, S. S., Rahman, M. M., & Hossain, M. A. (2022). Bergey’s manual of systematic bacteriology (5th ed.).

Humphreys, H., & Coleman, D. C. (2020). Impact of hospital design on the prevention of hospital-acquired infections: A narrative review. Journal of Hospital Infection, 105(4), 587–597.

International Agency for Research on Cancer (IARC). (2020). Volatile organic compounds: Health risks in healthcare environments. WHO Press.

Kowalski, W. J., & Bahnfleth, W. P. (2021). Airborne microbial control in hospital environments. ASHRAE Journal, 63(10), 22–30.

Lemos, A. C. S., Pereira, L. P. F., & Ribeiro, R. S. (2024). Characterization of airborne fungi in tertiary hospital environments: A focus on infection control. International Journal of Environmental Health Research, 34(1), 102–114.

Lemos, M. S. C. D., Higa Junior, M. G., Paniago, A. M. M., Melhem, M. D. S. C., Takahashi, J. P. F., Fava, W. S., & Chang, M. R. (2024). Aspergillus in the indoor air of critical areas of a tertiary hospital in Brazil. Journal of Fungi, 10(8), 538.

Li, Y., Leung, G. M., Tang, J. W., Yang, X., Chao, C. Y. H., Lin, J. Z., Lu, J. W., Nielsen, P. V., Niu, J., Qian, H., Sleigh, A. C., Su, H. J. J., Sundell, J., Wong, T. W., & Yuen, P. L. (2007). Role of ventilation in airborne transmission of infectious agents in the built environment: A multidisciplinary systematic review. Indoor Air, 17(1), 2–18.

Megri, A. C., Bouziane, M., & Abdullahi, M. (2022). Exposure assessment of bioaerosols in healthcare environments: Risks and control strategies. Environmental Advances, 9, 100287.

Megri, A. C., Bråbäck, L., & Forsberg, B. (2022). Exposure to indoor air pollution and respiratory health in hospital settings. BMC Pulmonary Medicine, 22, 271.

Morakinyo, O. M., Ezekiel, O. A., & Okechukwu, K. C. (2022). Indoor air quality and infection risk management in healthcare environments: A review. Environmental Science and Health Journal, 14(2), 87–103.

Morakinyo, O. M., Mokgobu, M. I., Mukhola, M. S., & Hunter, R. P. (2022). Health risk assessment of indoor air quality in hospital environments: A review. International Journal of Environmental Research and Public Health, 19(6), 3453.

National Environmental Standards and Regulations Enforcement Agency (NESREA). (2011). National Environmental (Air Quality Control) Regulations. Federal Government of Nigeria.

Nwachukwu, C. U., Eze, S. O., & Okonkwo, U. C. (2019). Assessment of volatile organic compounds in indoor air of Nigerian hospitals. Journal of Environmental Toxicology and Health Sciences, 11(2), 29–40.

Ogunlowo, S. A., Adetayo, J. O., & Nwogu, C. C. (2022). Sulphur dioxide trends and mitigation measures in the Niger Delta. Environmental Monitoring and Assessment, 194(3), 221–230.

Okafor, U. C., Nwankwo, C. E., & Eze, J. I. (2021). Microbiological quality assessment of indoor environments of major departments in a medical centre in Abia State, Nigeria. Nigerian Journal of Microbiology, 35(2), 5965–5976.

Onakoya, A. J., Adewuyi, G. O., & Ede, P. N. (2020). Airflow and pollutant dispersion in hospital indoor environments: A case study of the Niger Delta region. Journal of Environmental Protection, 11(5), 343–355.

Onmek, C., Anukul, N., & Chomanee, J. (2022). Bacterial and fungal contamination levels in hospital air: A systematic review. Asian Journal of Environmental Health, 19(3), 145–156.

Onmek, N., Kongcharoen, J., Singtong, A., Penjumrus, A., & Junnoo, S. (2022). Environmental factors and microbial contamination in hospital indoor air: A case study. Journal of Infection and Public Health, 15(4), 512–518.

Otter, J. A., & French, G. L. (2010). The role played by contaminated surfaces in the transmission of nosocomial pathogens. Infection Control & Hospital Epidemiology, 31(7), 687–699.

Otter, J. A., Mutters, N. T., Tacconelli, E., Gikas, A., & Holmes, A. H. (2021). Controlling the transmission of Staphylococcus aureus in healthcare settings: A review. Clinical Microbiology and Infection, 27(2), 201–208.

Oyeleke, S. B., & Manga, S. B. (2008). Essentials of laboratory practicals in microbiology. Tobest Publishers.

Standards Organisation of Nigeria (SON). (2015). Standards for indoor air quality in public and health facilities. SON.

Sorouri, Sh., Ahman Tehran, H., Parhoon, M., Saeidi, M. (2025). Air pollution in hospitals: A critical public health emergency and strategies for improving indoor air quality and patient safety. Health Provid:5(1)15-34. Doi10.22034/HP.2025500289.1060.

Ukpebor, E. E., & Ede, P. N. (2017). Hydrogen sulphide concentration in hospital indoor air and associated health risks. Environmental Health Review, 61(4), 98–106.

United Nations Environment Programme (UNEP). (2023). Air pollution and health.

Uzochukwu, C. I., Okeke, P. O., & Nweke, I. C. (2022). Fungal air quality of public and hospital environments in humid tropical regions. Nigerian Journal of Mycology and Environmental Health, 3(2), 51–63.

World Health Organization (WHO). (2022). WHO guidelines on core components of infection prevention and control programmes at the national and acute health care facility level.

World Health Organization (WHO). (2023). WHO fungal priority pathogens list to guide research, development and public health action.